# Professional Indirect Pool Heater

## Powered by XTherm®

## 1.0-1.5-2.0 MMBTUH Models

# Professional Indirect Pool Heater

## Powered by XTherm®

## 1.0-1.5-2.0 MMBTUH Models

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

96% Thermal Efficiency at Full Rate; Up to 99% at Part Load

VERSA IC® Modulating Controller

7 Inch HD Capacitive Color Touch Screen Display

Full Electronic Modulation, Constant Ratio 7:1 Turndown

Full Safety Diagnostics with History

PVC Venting

Modbus RTU BMS Port

Maximum Pool/Spa Water Temperature: 104°F

Limited Twenty-Five-Year Thermal Shock Warranty

Low NOx – Meets SCAQMD Rule 1146.2

Limited Ten-Year Primary Heat Exchanger Warranty

Proudly Assembled in the USA

Limited Ten-Year Secondary Heat Exchanger Warranty

Limited 3/5-Year Indirect Heat Exchanger Warranty

#### Heat Exchanger

Headers

Cast Iron

ASME H Stamped; 160 PSIG MAWP

National Board Listed

Copper Fin Tubing

ASME Powder-Coated Tube Sheet

Silicone High-Temp O-Rings

ASME Pressure Relief Valve

30 PSIG – Standard

Air Vent, Manual

T&P Gauge

Stainless Steel Secondary Heat Exchanger

Stainless Steel Evaporator Plate

Indirect Heat Exchanger

- Cupro-Nickel

- Titanium

Boiler Pump: 120V, 1, 60Hz

Indirect Pump: 115/230V, 1Ø, 60Hz

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

Versa IC® Integrated Control

Ignition Module

3-Try – Standard

C-6 Single-Try

Hot Surface Ignition (HSI)

Remote Flame Sensor

Adjustable Auto High Limit, 100-240°F

Adjustable Manual High Limit, 200°F

Low Water Cut-Off, Remote Probe

Low Gas Pressure Switch, Manual Reset

High Gas Pressure Switch, Manual Reset

Low Water Pressure Switch

On/Off Power Switch

Flow Switch (2)

Fixed Auto Limit – Pool Return

Blocked Vent Pressure Switch

Freeze Protection

Alarm Dry Contact

Programmable Pump Time Delays

7 Inch Color HD Touch Screen Display

Water Temperature Sensors (4)

Cold Water Protection – Built In

Blocked Condensate Switch

Modbus RTU BMS Port (Up to 115K Baud Rate, see Cat. No. 5000.73)

B-85   BMS Gateway, Modbus RTU to Modbus TCP, N2 Metasys, BACnet IP, or BACnet MS/TP

B-86   BMS Gateway, Modbus RTU to LonWorks

#### Burner

Radially-Fired Knitted Burner

#### Gas Train

Fuel

Natural Gas

Propane (HD-5)

Dual-Seat Combination Valve

Manual Shut-Off Firing Valve

Electronic Modulation Firing Mode (H7-)

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

PVC Vent Adapter (Includes Manual Vent Limit)

Mounted Condensate Treatment Kit

Rear Connections (Water, Gas, Vent, Electrical, Comb. Air, Cond. Drain)

Internal Combustion Air Filter

Front Connection Low Voltage Wiring

Indirect Pool Heat Exchanger

Expansion Tank

Manual Air Bleed Valve

#### Venting

Vent Termination, Cat IV

#### Options

E-15	Boiler Alarm Buzzer

F-14	System Flow Switch

M-1	Motorized Safety Valve

#### Additional Options and Accessories

# Professional Indirect Pool Heater

## Powered by XTherm®

## 1.0-1.5-2.0 MMBTUH Models						Model:

CLEARANCES (all models) (in.)

|  | Front | Rear | Right | Left | Top | Floor | Vent |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Certified Minimum | 24 | 12 | 1 | 1 | 0 | 0 | 1 |
| Minimum Service | 24 | 36 | 24 | 1 | 10 | N/A | N/A |

† Separate power connections are factory supplied and separate supply breakers must be field supplied.

** Current draw is for boiler only (Supply breaker must have delayed trip).

† Separate power connections are factory supplied and separate supply breakers must be field supplied.

** Current draw is for boiler only (Supply breaker must have delayed trip).

| Model | Amp Draw** (120V) |  |  |
| --- | --- | --- | --- |
|  | Boiler † | Boiler Pump † | Indirect Pump † |
| 1005A | 12** | 10 | > 7 |
| 1505A | 12** | 14 | 10.8 |

| Model (H7-) | MBTUH |  | Dimensions (in.) |  |  |  |  |  |  | Ship Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | In | Out | B Height | E | G* NPT | K Flue Ø | N C/A Ø | P | R |  |
| 1005A | 999 (292.7) | 969 (283.9) | 55-1/4 (1403) | 47 (1194) | 1-1/4 | 6 | 6 | 47-1/8 (1197) | 8-5/16 (211) | 1343 (609) |
| 1505A | 1500 (439.6) | 1455 (426.4) | 67-1/8 (1705) | 59 (1499) | 1-1/4 | 8 | 8 | 59-1/8 (1502) | 8-3/16 (208) | 1448 (657) |

* For Propane Gas, all models are 1” NPT.

* For Propane Gas, all models are 1” NPT.

Note: Ratings are shown for elevations up to 4,500 feet. For installations at elevations

Above 4,500 feet, please consult the factory for additional instructions.

Note: Ratings are shown for elevations up to 4,500 feet. For installations at elevations

Above 4,500 feet, please consult the factory for additional instructions.

# Professional Indirect Pool Heater

## Powered by XTherm®

## 1.0-1.5-2.0 MMBTUH Models						Model:

| Model | Amp Draw** (120V) |  |  |
| --- | --- | --- | --- |
|  | Boiler † | Boiler Pump † | Indirect Pump † |
| 2005A | 12** | 10 | > 15 |

† Separate power connections are factory supplied and separate supply breakers must be field supplied.

** Current draw is for boiler only (Supply breaker must have delayed trip).

† Separate power connections are factory supplied and separate supply breakers must be field supplied.

** Current draw is for boiler only (Supply breaker must have delayed trip).

| Model (H7-) | MBTUH |  | Dimensions (in.) |  |  |  |  |  |  | Ship Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | In | Out | B Height | E | G* NPT | K Flue Ø | N C/A Ø | P | R |  |
| 2005A | 1999 (585.5) | 1939 (568.2) | 81-1/8 (2061) | 72 (1829) | 2 | 8 | 8 | 73-1/8 (1857) | 8-3/16 (208) | 1930 (875) |

* For Propane Gas, all models are 1” NPT.

* For Propane Gas, all models are 1” NPT.

Note: Ratings are shown for elevations up to 4,500 feet. For installations at elevations

Above 4,500 feet, please consult the factory for additional instructions.

Note: Ratings are shown for elevations up to 4,500 feet. For installations at elevations

Above 4,500 feet, please consult the factory for additional instructions.

# Professional Indirect Pool Heater

## Powered by XTherm®

## 1.0-1.5-2.0 MMBTUH Models						Model:

Anchoring Details

Anchoring Details

Models 1005A – 1505A

| TDS Limit | Chlorine Limit | pH |
| --- | --- | --- |
| 3,000 PPM | 2 – 3 PPM | 7.6 – 7.8 |

Water Chemistry

Models 2005A