Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     	 Outdoor

LOW NOx

Less than 40 nanograms per joule

EFFICIENT

82% thermal efficiency – highest of any atmospheric boiler available today

THERMAL SHOCK PROOF

Twenty-year warranty against thermal shock damage
up to 150°F differential

Maximum operating temperature: 230°F

LIGHTWEIGHT

A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

Cuts fuel costs substantially because the standby and
radiation losses normal to other boilers and
tank-type water heaters are eliminated

LOW WATER OPERATING TEMPERATURE

Operates with water temperature as low as
105°F without condensing

#### Heat Exchanger

ASME Inspected and Stamped
160 PSIG

National Board Approved

Headers

Cast Iron Glass-lined – Standard

Bronze – Option A-1

Finned Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone O-Rings

45 PSIG ASME Pressure Relief Valve

Temperature and Pressure Gauge, Shipped Loose

Water Connections

Left Hand – Standard

Right Hand – Option A-6

Flow Configuration – Two-pass

Pump – Optional

Mounted, 1/8 HP, 120 Volt, 1(( 60 Hz

#### Controls

120V, 60Hz, 1 Ph Power Supply

120/24V Transformer

100% Pilot Shut-off/Lockout

Electronic, Intermittent Ignition (IID) Pilot

High Limit Control, Manual Reset

#### Controls (cont'd)

On/Off Switch

Flow Switch

Economaster II Pump Time Delay

Electronic Outdoor Reset Control

( Std. on Models 181 & 261)

#### Gas Train

Natural Gas

Manual Main Gas Shut-off Cock

Main Gas Pressure Regulator

Redundant Safety Shut-off Valve

Control Valve

Firing Mode

On/Off (H4)

Two-stage Firing (H3)

Design Certified ANSI Z21.13/CSA 4.9

#### Construction

Stainless Steel, Fan Assisted Burners

Front Controls

Polytuf Powder Coat Finish

Stackless Top

8" Base – Standard

Vent Selection

Stackless Top – Option D-11

Power Vent, Loose – Option D-2

#### Temperature Controls

B-6	2-stage Aquastat – 100-200(F

B-26	2-stage Digital Controller

B-27	2-stage Digital Controller, Outdoor Reset

B-___,Temp Tracker Digital 
Controller, 2 stages

B-___,Temp Tracker Digital Controller, 4 stages

B-42   Electronic Outdoor Reset

Controller. (Std. on Models 181 & 261)

#### Additional Safety Controls

F-10	Low Water Cut-off Probe

I-1	High Limit Control, Auto Reset

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

#### Regulatory Agency Requirements

Raytherm - Type H

Hydronic Heating Boilers - Outdoor	Model

# Text boxes

Low NOx

# Raytherm® - Type H

# Hydronic Heating Boilers

# Models 181-401 - Outdoor

Low NOx

|  |  |  |  | Shipping Weight |
| --- | --- | --- | --- | --- |
| Model | MBTUH | MBTUH | Width | (Lbs.) - Approx. |
| No. | Input | Output | A | No Pump | w/ Pump |
| H-181 | 181 | 145 | 18-1/4" | 191 | 221 |
| H-261 | 264 | 211 | 22-3/8" | 214 | 244 |
| H-331 | 334 | 267 | 25-3/4" | 234 | 264 |
| H-401 | 399 | 319 | 29-1/4" | 253 | 283 |

NOTE:	Ratings shown are for elevations up to 2,000 feet for indoor or outdoor installations. For elevations over 2,000 feet, reduce ratings at the rate of 4% for each 1,000 feet above sea level.

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com

BOILER RATE OF FLOW AND PRESSURE DROP

| Model | 10° (T | 20° (T | 30° (T | 40°(T |
| --- | --- | --- | --- | --- |
| No. | GPM | (P FT | GPM | (P FT | GPM | (P FT | GPM | (P FT |
| H-181 | 29 | 4.2 | N/A | N/A | N/A | N/A | N/A | N/A |
| H-261 | 42 | 8.5 | 21 | 2.2 | N/A | N/A | N/A | N/A |
| H-331 | N/A | N/A | 27 | 3.4 | N/A | N/A | N/A | N/A |
| H-401 | N/A | N/A | 32 | 5.2 | 21 | 2.3 | N/A | N/A |

N/A – Not Applicable

BOILER RECOVERY RATES

| Model | Temperature Rise |
| --- | --- |
| No. | 10°F | 20°F | 30°F | 40°F | 50°F | 60°F | 80°F | 100°F |
|  | Gallons Per Hour |
| H-181 | 1794 | 897 | 598 | 448 | 359 | 299 | 224 | 179 |
| H-261 | 2618 | 1309 | 873 | 655 | 524 | 436 | 327 | 262 |
| H-331 | 3321 | 1661 | 1107 | 830 | 664 | 554 | 415 | 332 |
| H-401 | 3964 | 1982 | 1321 | 991 | 793 | 661 | 495 | 396 |

BOILER RATE OF FLOW AND PRESSURE DROP

| Model | 10° (T | 20° (T | 30° (T | 40°(T |
| --- | --- | --- | --- | --- |
| No. | GPM | (P FT | GPM | (P FT | GPM | (P FT | GPM | (P FT |
| H-181 | 30 | 4.2 | N/A | N/A | N/A | N/A | N/A | N/A |
| H-261 | 43 | 8.5 | 22 | 2.2 | N/A | N/A | N/A | N/A |
| H-331 | N/A | N/A | 27 | 3.4 | N/A | N/A | N/A | N/A |
| H-401 | N/A | N/A | 33 | 5.2 | 22 | 2.3 | N/A | N/A |

N/A – Not Applicable