Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

EFFICIENT

82% thermal efficiency – highest of any atmospheric water heater available today

THERMAL SHOCK PROOF

Twenty-year warranty against thermal shock damage
up to 150°F differential

Maximum operating temperature: 200°F

LIGHTWEIGHT

A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

Cuts fuel costs substantially because the standby and
radiation losses associated with other tank-type water 
heaters are eliminated

LOW WATER OPERATING TEMPERATURE

Operates with water temperature as low as
105°F without condensing

#### Heat Exchanger

ASME Inspected and Stamped
160 PSIG

National Board Approved

Headers

Bronze – Standard

Glass-lined Cast Iron – Option A-2

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

150 PSIG – Option A-16

Temperature and Pressure Gauge,
Shipped Loose

Water Connections

Left Hand – Standard

Right Hand – Option A-6

Two-pass Flow Configuration

Pump – Optional

Mounted, 1/8 HP, 120 VAC, 1(, 60 Hz

#### Controls

120V, 60Hz, 1 Ph Power Supply

120/24V Transformer

100% Pilot Shut-off/Lockout

Electronic, Intermittent Ignition (IID) Pilot

High Limit Control, Manual Reset – 200°F

#### Controls (cont.)

On/Off Switch

Flow Switch

Economaster II Pump Time Delay

#### Gas Control Train

Manual Main Gas Shut-off Cock

Main Gas Pressure Regulator

Redundant Safety Shut-off Valve

Control Valve

Firing Mode

On/Off (WH1)

2-stage (WH3)

Mechanical Modulation (WH2)

Fuel

Natural Gas

Propane Gas

Design Certified ANSI Z21.10.3/
CSA 4.3

#### Construction

Front Controls

Stainless Steel Burners

PolyTuf Powder Coat Finish

Vent Selection

Indoor Drafthood – Option D-10

Outdoor Stackless Top – 
Option D-11

Base – Optional

Combustible Floor Shield – 
Option J-1

CSA Low Lead Certified ≤ .25% Lead

#### Temperature Controls

B-2	Single-Stage Tankstat 
(100-180°F)

B-3	2-Stage Tankstat (100-180°F)

B-26	2-Stage Digital

B-21	4-Stage Digital

#### Additional Safety Controls

F-10	Low Water Cut-off Probe

I-3	High Limit Control, Auto Reset, 180°F

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

Raytherm - Type WH

Models 182-400	Model

# Text boxes

# Raytherm® - Type WH

## Water Heaters
Commercial

Models 182-400

Proudly Assembled in the USA

Indoor Model Illustrated

|  |  |  | Dimensions (Inches) | Shipping Weight |
| --- | --- | --- | --- | --- |
| Model | MBTUH | MBTUH | Width | Height |  | Flue Dia. | (Lbs.) – Approx. |
| No. | Input | Output | A | C | J | K | No Pump | w/ Pump |
| WH-182 | 181 | 148 | 18-1/4 | 62-5/8 | 12-1/16 | 6 | 191 | 221 |
| WH-260 | 264 | 216 | 22-3/8 | 62-7/8 | 11-1/8 | 7 | 214 | 244 |
| WH-330 | 334 | 274 | 25-3/4 | 63-3/4 | 10-3/4 | 8 | 234 | 264 |
| WH-400 | 399 | 327 | 29-1/4 | 65-3/8 | 12-1/2 | 9 | 253 | 283 |

NOTE:	Ratings shown are for elevations up to 2,000 feet for indoor or outdoor installations. For elevations over 2,000 feet, reduce ratings 4% for each 1,000 feet above sea level.

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com

HEATER RECOVERY RATES

|  | Temperature Rise |
| --- | --- |
| Model | 10°F | 20°F | 30°F | 40°F | 50°F | 60°F | 80°F | 100°FF |
| No. | Gallons Per Hour |
| WH-182 | 1794 | 897 | 598 | 448 | 359 | 299 | 224 | 179 |
| WH-260 | 2618 | 1309 | 873 | 655 | 524 | 436 | 327 | 262 |
| WH-330 | 3321 | 1661 | 1107 | 830 | 664 | 554 | 415 | 332 |
| WH-400 | 3964 | 1982 | 1321 | 991 | 793 | 661 | 495 | 396 |

HEATER RATES OF FLOW AND PRESSURE DROPS

| Model | 10° ∆T | 20° ∆T | 30° ∆T | 40°∆T |
| --- | --- | --- | --- | --- |
| No. | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) |
| WH-182 | 30 | 4.2 | N/A | N/A | N/A | N/A | N/A | N/A |
| WH-260 | 44 | 8.5 | 22 | 2.2 | N/A | N/A | N/A | N/A |
| WH-330 | N/A | N/A | 28 | 3.4 | N/A | N/A | N/A | N/A |
| WH-400 | N/A | N/A | 33 | 5.2 | 22 | 2.3 | N/A | N/A |

N/A – Not Applicable