# MVB®

# Type WH

## Water Heaters

## Models 2503-4003

# MVB®

# Type WH

## Water Heaters

## Models 2503-4003

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 85% Thermal Efficiency at Full Rate

- 100% Factory Fire-Tested

- VERSA IC® Integrated Controller with 7” Color Touch Screen Display

- Full Electronic Modulation, 60% Minimum Fire under Normal Conditions

- Full Safety Diagnostics with History

- Status Display LED Lights

- Ultra Low NOx (BAAQMD Reg. 9, Rule 7 Approved)

- Cascade up to 4 Heaters – No External Sequencer Required

- Modbus RTU BMS Port

- Maximum Outlet Water Temperature: 200°F

- Maximum Tank Setpoint: 150°F

Proudly Assembled in the USA

Proudly Assembled in the USA

Minimum Inlet Water Temperature: 120°F

- Limited Five-Year Copper/Ten-Year Cupro-Nickel Heat Exchanger Warranty

#### Heat Exchanger

Bronze Headers

ASME HLW Stamped; 160 PSIG MAWP

National Board Approved

Fin Tubing

Copper – Standard

A-3 Cupro-Nickel

ASME Powder-Coated Tube Sheet

Silicone High-Temp O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

150 PSI Air Vent, Auto (2)

T&P Gauge

4-Pass Heat Exchanger

Stainless Steel Evaporator Plate

4-Inch Grooved Copper Water Connections

#### Control

240V, 60Hz, 1Ø, Power Supply

240/120V 60Hz Transformer

240/24V 60Hz Transformer

VERSA IC® Integrated Control

Hot Surface Ignition (HSI)

Ignition Module

3-Try – Standard

C-6 - Single-Try

Remote Flame Sensor

Fixed High Limit, Manual Reset, 200°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Freeze Protection

Alarm Dry Contact

High Gas Pressure Switch

Pump outputs – Pilot Duty

Water Heater

System

Programmable Pump Time Delays

7” Color HD Touch Screen Display

Modulating Temperature Control, 60% minimum fire

Water Temperature Sensors (3)

Cold Water Protection Function

- CWR Variable-Speed Pump

Modbus RTU BMS Port (Up to 115K Baud, See    Cat. 5000.73)

- B-85 – BMS Gateway – BACnet MS/TP,   BACnet IP, N2 Metasys or Modbus TCP

- B-86 – BMS Gateway - LonWorks

#### Burner

Radially-Fired Knitted Burner

#### Gas Train

Fuel

Natural Gas

Propane (HD-5)

Dual-Seat Combination Valve

Manual Shut Off Firing Valve

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

Rear Connections (Water, Gas, Vent, Electrical, Comb. Air)

Combustion Air Filter

Front Connection Low Voltage Wiring

Design Certified ANSI Z21.10.3/CSA 4.3

CSA Low Lead Certified ≤.25% Lead

#### Venting

Vent Termination

D-11 Outdoor or Indoor, Vertical – (Cat IV) 	D-15 Indoor, Horizontal – (Cat IV)

Extractor – Optional

- By others

- Not Required

#### Options

D-11	Outdoor Vent Cap with Outdoor Filter Cover

D-22	Truseal Air Intake Box, Indoor

F-10	Low Water Cut-Off, Remote Probe

I-6	High Limit, Auto Reset, Adj., 
100-200°F

I-12	High Limit, Manual Reset, Adj., 100-200°F

S-1	Low Gas Pressure Switch, 
Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

MVB® - Type WH

Models 2503-4003	Model

Clearances (in)

|  | Front | Rear | Side | Other Side | Top | Floor | Vent |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Combustible Minimum | 24 | 12 | 1 | 1 | 0 | 0 | 1 |
| Minimum Service | 30 | 36 | 24* | 1 | 12 | N/A | N/A |

*Service Clearance can be right side or left side.

NOTE:  Must be used with properly sized storage tank for proper operation.

NOTE:  Must be used with properly sized storage tank for proper operation.

| Model (WH7-) | MBTUH |  | Dimensions (in) |  |  |  |  |  |  | Amp Draw | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | B Height | D | E | K Flue Ø | M | N C/A Ø | T |  |  |
| 2503 | 2501 | 2126 | 68-1/8 | 64-1/16 | 64-7/8 | 10 | 26-3/4 | 10 | 53-1/4 | 12 | 1410 |
| 3003 | 3000 | 2550 | 73-1/8 | 69-1/16 | 69-7/8 | 10 | 29-1/4 | 10 | 58-1/4 | 15 | 1450 |
| 3503 | 3500 | 2975 | 78-1/8 | 74-1/16 | 74-7/8 | 12 | 31-3/4 | 12 | 63-1/4 | 17 | 1550 |
| 4003 | 4000 | 3400 | 83-1/8 | 79-1/16 | 79-7/8 | 12 | 34-1/4 | 12 | 68-1/4 | 20 | 1660 |

*Water connections are grooved copper tube.

Amp draw is for heater only and does not include pumps or accessories.

MVB® - Type WH

Models 2503-4003	Model

NOTE:  Must be used with properly sized storage tank for proper operation.

NOTE:  Must be used with properly sized storage tank for proper operation.

|  |  | WATER HARDNESS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | SOFT * |  |  |  |  | MEDIUM |  |  |  |  | HARD* |  |  |  |  |
| Model (WH7-) |  | 3-4 Grains Per Gallon‡ |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | MBTUH Input | ΔT (°F) | GPM | ΔP† (ft wc) | MTS (in) | SHL (ft wc) | ΔT (°F) | GPM | ΔP† (ft wc) | MTS (in) | SHL (ft wc) | ΔT (°F) | GPM | ΔP† (ft wc) | MTS (in) | SHL (ft wc) |
| 2503 | 2501 | 29 | 147 | 6.6 | 4 | 7.9 | 20 | 213 | 11.7 | 4 | 14.4 | 16 | 264 | 15.7 | 4 | 20.0 |
| 3003 | 3000 | 29 | 176 | 11.0 | 4 | 12.8 | 20 | 255 | 21.7 | 4 | 25.6 | 19 | 264 | 23.1 | 4 | 27.3 |
| 3503 | 3500 | 29 | 205 | 16.3 | 4 | 18.8 | 23 | 264 | 26.8 | 4 | 31.0 | 23 | 264 | 26.8 | 4 | 31.0 |
| 4003 | 4000 | 29 | 234 | 25.6 | 4 | 28.9 | 26 | 264 | 33.5 | 4 | 37.7 | 26 | 264 | 33.5 | 4 | 37.7 |

* Cupro-Nickel tubes are required for hard water applications and water softened below 3 GPG.

** Water treatment is required when hardness exceeds 25 GPG.

‡ Water softened below 3 GPG has been known to be aggressive and may damage the appliance.

†ΔP is based upon type “L” copper tubing.

264 GPM is maximum allowable flow.

Do not exceed ΔT of 29 ºF.

| Model (WH7) | RECOVERY RATES (GPH) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |
|  | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |
| 2503 | 12884 | 8589 | 6442 | 5154 | 4295 | 3681 | 3221 | 2863 | 2577 |
| 3003 | 15455 | 10303 | 7727 | 6182 | 5152 | 4416 | 3864 | 3434 | 3091 |
| 3503 | 18030 | 12020 | 9015 | 7212 | 6010 | 5152 | 4508 | 4007 | 3606 |
| 4003 | 20606 | 13737 | 10303 | 8242 | 6869 | 5887 | 5152 | 4579 | 4121 |

Base Anchor Bolt Pattern

Raypak, Inc. • Eastman Avenue, Oxnard, CA 93030 • (805) 278-5300 • (805) 872-9725 • www.raypak.com

Raypak, Inc. • Eastman Avenue, Oxnard, CA 93030 • (805) 278-5300 • (805) 872-9725 • www.raypak.com