Job:


# Hi Delta FlexGas® - Type WH

## Dual-Fuel Water Heaters Models 992CD-2342CD

Engineer:

Contractor:

Prepared By:       Date:

Model:       Indoor/Outdoor:       MBTUH Input:

* 100% Factory Fire Tested
* Thermal Efficiency: Up to 85%
* Versa IC® Controller with LCD Display
* Maximum Setpoint: 150°F
* Maximum Outlet Temperature: 200°F
* Minimum Non-Condensing Inlet Temperature: 105°F
* Thermal-Shock Proof Heat Exchanger
* Limited Twenty-Year Thermal Shock Warranty
* Limited Ten-Year Cupro-Nickel Heat Exchanger Warranty
* Limited Five-Year Copper Heat Exchanger Warranty
* Full Safety Diagnostics with Fault History
* PolyTuf Powder Coated Cabinet

Patent Nos. 6,904,873 & 7,044,124; other patents pending

* No Combustible Floor Shield Required
* Fan-Assisted
* Patented Burner Security Blanket



Proudly Assembled in the USA

* Ultra-Low NOx – SCAQMD 1146.2 Certified (992C – 1802C)
* Cascade up to 4 Heaters – No External Sequencer Required

#### Heat Exchanger

* Headers

Brass – Standard

A-2 Glass-Lined Cast Iron

* ASME Inspected and HLW Stamped  
  160 PSIG Working Pressure
* National Board Approved
* Fin Tubing

Copper (Std.) 85%

Cupro-Nickel 83.1%

* ASME Steel Tube Sheet
* Silicone High-Temp. O-Rings
* ASME Pressure Relief Valve

125 PSIG – Standard

      PSIG – Optional

* Temperature and Pressure Gauge
* Water Connections

Left – Standard

#### A-6 Right Hand

#### Controls

* 120V, 60Hz, 1∅ Power Supply
* 120/24V 60Hz Transformer
* Versa IC® Integrated Control
* 100% Shut-Off/Lockout
* Hot Surface Ignition
* Ignition Module

3-Try – Standard

C-6 Single Try

* Remote Flame Sensor
* Fixed High Limit, Manual Reset 240°F
* On/Off Power Switch
* Flow Switch
* Blocked Vent Pressure Switch
* Combustion Air Proving Switch
* Programmable Pump Time Delays
* Heater
* Recirculation
* Enable/Disable

#### Raypak-Rheem%20logo_submittalsControls – cont.

* LCD Display; Status, Fault and Diagnostics
* Cold Water Protection Function

Optional CWR Variable-Speed Pump

(See Cat. 5000.73)

* Modbus RTU BMS Port (Up to 115K Baud, See Cat. 5000.73)

B-85 – BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

B-86 – BMS Gateway - LonWorks

#### Gas Train

* Manual Gas Shut-Off Valve(s)
* Combo Valve(s)
* Firing Mode

3-Stage (WH8): Model 992C

4-Stage (WH9): Models 1262C – 2342C

* Natural/Propane Gas
* Design Certified - ANSI Z21.10.3/CSA 4.3

#### Construction

* Indoor/Outdoor Construction
* Enclosed Front Controls
* Powder Coat Finish
* CSA Low Lead Certified (≤ .25% Lead)

#### Venting

Vent Category I/III Cupro-Nickel

Vent Category II/IV Copper

* Vent Location

Top – Standard

D-14 Rear

* Vent Termination Cap

D-11 Outdoor

D-15 Indoor, Horizontal

 Indoor, Vertical (by others)

* Combustion Air

D-17 In-Line Filter Kit (TruSeal only)

D-16 Air Intake Elbow

#### Venting – cont.

* Extractor – Optional

By others

Not required

#### Burner

Ultra-Low NOx: Less than 20 PPM

**Options**

D-21 TruSeal® Direct Vent

F-10 Low Water Cut-Off, Remote Probe

I-1 High Limit Control, Auto Reset

P-   Pump:       HP, 120V, 1∅, 60Hz

Bronze  
 Mounted  Loose

Front  Rear

S-1 Low Gas Pressure Switch, Manual

S-2 High Gas Pressure Switch, Manual

X-1 SureRack® Kit

X-2 SureRack Add-on

Additional Options or Accessories

#### Multi-Boiler Temperature Controllers

TempTracker Mod+ Hybrid

B-36, 2-4 Heaters

B-37, 5-10 Heaters


B-38, 11-16 Heaters

B-39 EMS 4-20mA Remote Setpoint Interface Module

B-62 BACnet MS/TP Interface

#### Hi Delta FlexGas – Type WH Models 992CD-2342CD Model \_     \_\_\_\_\_

Raypak, Inc. ▪ 2151 Eastman Avenue, Oxnard, CA 93030 ▪ (805) 278-5300 ▪ Fax (800) 872-9725 ▪ www.raypak.com



NOTE: Pump location varies based on model and application.

|  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | **SPECIFICATIONS** | | | | | | | | | |
| **Model** | **MBTUH** | | | **Firing**  **Stages** | **A**  **Width** | **K** | **T** | **W** | **Amp.**  **Draw\*** | **Approx.**  **Shipping**  **Wt. (Lbs.)** |
| **Input** | **Output**  **85%** | **Output**  **83.1%** |
| 992CD | 990 | 842 | 823 | 3 | 57-1/8 | 10 | 10 | 16-13/16 | <12 | 900 |
| 1262CD | 1260 | 1071 | 1047 | 4 | 68-1/2 | 12 | 20-9/16 | 1010 |
| 1532CD | 1530 | 1301 | 1271 | 4 | 79-7/8 | 12 | 24-3/8 | 1225 |
| 1802CD | 1800 | 1530 | 1496 | 4 | 91-1/8 | 14 | 28-1/8 | 1350 |
| 2072CD | 2070 | 1760 | 1720 | 4 | 102-1/2 | 14 | 31-15/16 | 1450 |
| 2342CD | 2340 | 1989 | 1945 | 4 | 113-7/8 | 16 | 35-11/16 | 1520 |

\*Without pump.

NOTES: 1. Dimensions are in inches.

2. Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

3. Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

#### Hi Delta FlexGas – Type WH Models 992CD-2342CD Model

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Model** | **83.1% System Flow and Head Loss** | | | | | | | | | | | | | | |
| **3-4 Grains Per Gallon** | | | | | **5-15 Grains Per Gallon** | | | | | **16-25\*\* Grains Per Gallon** | | | | |
| ΔT  (°F) | GPM | ΔP  (FT WC) | MTS  (IN) | SHL  (FT WC) | ΔT  (°F) | GPM | ΔP  (FT WC) | MTS  (IN) | SHL  (FT WC) | ΔT  (°F) | GPM | ΔP  (FT WC) | MTS  (IN) | SHL  (FT WC) |
| 992CD | 28 | 60 | 2.7 | 2 1/2 | 5.2 | 17 | 98 | 7.3 | 2 1/2 | 13.3 | 13 | 132 | 13.1 | 2 1/2 | 23.6 |
| 1262CD | 28 | 75 | 4.8 | 2 1/2 | 8.5 | 18 | 115 | 11.3 | 2 1/2 | 19.4 | 16 | 132 | 14.8 | 2 1/2 | 25.3 |
| 1532CD | 30 | 86 | 7.1 | 2 1/2 | 11.9 | 21 | 120 | 13.7 | 2 1/2 | 22.5 | 19 | 132 | 16.5 | 2 1/2 | 27.0 |
| 1802CD | 30 | 102 | 10.9 | 2 1/2 | 17.4 | 25 | 120 | 15.1 | 2 1/2 | 23.9 | 23 | 132 | 18.3 | 2 1/2 | 28.7 |
| 2072CD | 30 | 117 | 15.1 | 2 1/2 | 23.4 | 26 | 132 | 19.0 | 2 1/2 | 29.5 | 26 | 132 | 19.0 | 2 1/2 | 29.5 |
| 2342CD | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Model** | **85% System Flow and Head Loss** | | | | | | | | | | | | | | |
| **3-4 Grains Per Gallon** | | | | | **5-15 Grains Per Gallon** | | | | | **16-25\*\* Grains Per Gallon** | | | | |
| ΔT  (°F) | GPM | ΔP  (FT WC) | MTS  (IN) | SHL  (FT WC) | ΔT  (°F) | GPM | ΔP  (FT WC) | MTS  (IN) | SHL  (FT WC) | ΔT  (°F) | GPM | ΔP  (FT WC) | MTS  (IN) | SHL  (FT WC) |
| 992CD | 28 | 60 | 2.7 | 2 1/2 | 5.2 | 17 | 98 | 7.3 | 2 1/2 | 13.3 | 13 | 132 | 13.1 | 2 1/2 | 23.6 |
| 1262CD | 28 | 76 | 4.8 | 2 1/2 | 8.5 | 19 | 115 | 11.3 | 2 1/2 | 19.4 | 16 | 132 | 14.8 | 2 1/2 | 25.3 |
| 1532CD | 32 | 83 | 7.1 | 2 1/2 | 11.9 | 22 | 120 | 13.7 | 2 1/2 | 22.5 | 20 | 132 | 16.5 | 2 1/2 | 27.0 |
| 1802CD | 32 | 98 | 10.9 | 2 1/2 | 17.4 | 26 | 120 | 15.1 | 2 1/2 | 23.9 | 23 | 132 | 18.3 | 2 1/2 | 28.7 |
| 2072CD | 32 | 112 | 15.1 | 2 1/2 | 23.4 | 27 | 132 | 19.0 | 2 1/2 | 29.5 | 27 | 132 | 19.0 | 2 1/2 | 29.5 |
| 2342CD | 32 | 126 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 | 30 | 132 | 21.4 | 2 1/2 | 31.8 |

SHL includes 50 equivalent ft of tubing each way (100 total)

\*\* Must use optional cupro-nickel tubes. For hardness exceeding 25 GPG, must use water softener

Basis for minimum flow is 55 GPM or 30°F ∆T, 132 GPM for maximum flow

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Model** | **83.1% RECOVERY RATES (GPH)** | | | | | | | | |
| **Temperature Rise (°F)** | | | | | | | | |
| **20°** | **30°** | **40°** | **50°** | **60°** | **70°** | **80°** | **90°** | **100°** |
| 992CD | 4986 | 3324 | 2493 | 1994 | 1662 | 1425 | 1247 | 1108 | 997 |
| 1262CD | 6346 | 4231 | 3173 | 2538 | 2115 | 1813 | 1586 | 1410 | 1269 |
| 1532CD | 7706 | 5137 | 3853 | 3082 | 2569 | 2202 | 1926 | 1712 | 1541 |
| 1802CD | 9065 | 6044 | 4533 | 3626 | 3022 | 2590 | 2266 | 2015 | 1813 |
| 2072CD | 10425 | 6950 | 5213 | 4170 | 3475 | 2979 | 2606 | 2317 | 2085 |
| 2342CD | 11785 | 7857 | 5893 | 4714 | 3928 | 3367 | 2946 | 2619 | 2357 |

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Model** | **85% RECOVERY RATES (GPH)** | | | | | | | | |
| **Temperature Rise (°F)** | | | | | | | | |
| **20°** | **30°** | **40°** | **50°** | **60°** | **70°** | **80°** | **90°** | **100°** |
| 992CD | 5100 | 3400 | 2550 | 2040 | 1700 | 1457 | 1275 | 1133 | 1020 |
| 1262CD | 6491 | 4327 | 3245 | 2596 | 2164 | 1855 | 1623 | 1442 | 1298 |
| 1532CD | 7882 | 5255 | 3941 | 3153 | 2627 | 2252 | 1970 | 1752 | 1576 |
| 1802CD | 9273 | 6182 | 4636 | 3709 | 3091 | 2649 | 2318 | 2061 | 1855 |
| 2072CD | 10664 | 7109 | 5332 | 4265 | 3555 | 3047 | 2666 | 2370 | 2133 |
| 2342CD | 12055 | 8036 | 6027 | 4822 | 4018 | 3444 | 3014 | 2679 | 2411 |

Raypak, Inc. ▪ 2151 Eastman Avenue, Oxnard, CA 93030 ▪ (805) 278-5300 ▪ Fax (800) 872-9725 ▪ www.raypak.com