# XFyre® - Type H

## Condensing Heating Boilers
Models 300A-850A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- Stainless Steel Water-tube Construction

- 94% Thermal Efficiency at Full Rate

- VERSA IC® Modulating Controller

- LCD Status Display with Full Diagnostics and Fault Memory

- Cascade up to Four Heaters – No External Sequencer Required

- Modbus RTU BMS Port

- Soft Start, Electronic Modulation, 5:1 Turndown

- Maximum Outlet Water Temperature: 195ºF

- Maximum System Temperature: 190ºF

- 100% Factory Fire Tested

- Zero Clearance to Combustibles

- Indoor/Outdoor Construction Standard

- PVC, CPVC, Centrotherm™ Polypropylene or Stainless Venting Certified1

- Meets 2012 NOx Requirements (< 20 ppm)

Proudly Assembled in the USA

Limited Twenty-Five-Year Thermal Shock Warranty

- Limited Ten-Year Heat Exchanger Warranty

#### Heat Exchanger

All Stainless Steel Construction with Copper Connections

Gasketless Heat Exchanger Design

ASME H Stamped
160 PSIG Working Pressure

National Board Approved

ASME Pressure Relief Valve, Loose

45 PSIG – Standard (300 & 400)

60 PSIG – Standard (500 – 850)

PSIG – Optional

Temperature and Pressure Gauge,
Shipped Loose

#### Control

120V, 60Hz, 1Ø, Power Supply

VERSA IC with LCD display

Outdoor Reset with Indirect Priority

0-10 VDC input for BMS

Cascade up to 4 boilers

Remote Flame Sensor

High Limit, Manual Reset, Fixed, 200ºF

Alarm Dry Contact Connection

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Boiler, DHW & System Pump Contacts

Water Temperature Sensors (5)10kΩ   (3 shipped loose)

#### Burner

Spark Ignition (DSI)

Ultra-Low NOx: Less than 20 PPM

#### Gas Train

Fuel

Natural Gas

Propane

Dual-Seat Combination Valve

H7 Electronic Modulating Firing Mode

#### Construction

Indoor/Outdoor Construction

Front Controls Enclosed

PolyTuf Powder Coat Finish

Rear Connections (Electrical, Gas, Vent, Combustion Air)

Top Connections (Water)

Design Certified ANSI Z21.13/
CSA 4.9

Combustion Air Filter

Condensate Trap

CSA Low Lead Certified (≤.25% Pb)

#### Venting (PVC-CPVC-Centrotherm™ Polypropylene - Stainless1)

Vent Termination

D-11     Outdoor

D-15     Indoor, Horizontal

D-33     Polypropylene Adapter

Extractor - Optional

By others

Not required

#### Multi-Boiler System Controllers

B-36	TempTracker Mod+ Hybrid Digital

Controller, 2-4 Boilers, OA Reset

B-37	TempTracker Mod+ Hybrid Digital

Controller, 5-10 Boilers, OA Reset

B-38 	TempTracker Mod+ Hybrid Digital

Controller, 11-16 Boilers, OA Reset

#### Options

B-31	Well Assembly

B-32	Outdoor Air Sensor (1) 10kΩ

D-21 	TruSeal® Combustion Air Inlet (Mounted)

D-22 	TruSeal® Combustion Air Inlet (Loose)

F-10 	Low Water Cut-Off, Remote Probe

P-  	Pump:      HP, 120V,	1, 60Hz

Cast Iron

Bronze/SS

S-1/S-2  High/Low Gas Pressure Switch,

Manual Reset

Z-12	Condensate Neutralizer Kit

#### Regulatory Agency Requirements

Note 1: PVC venting on Models H7-700A and H7-850A is acceptable with system temperatures below 130°F only.

See I & O Manual Cat. 1000.65

XFyre® – Type H

Models 300A-850A	Model

|  | CLEARANCES (in.) |  |
| --- | --- | --- |
|  | Certified Minimum | Service Minimum |
| Front | 24 | 24 |
| Rear | 24 | 24 |
| Right | 0 | 0 |
| Left | 0 | 0 |
| Top | 12 | 24 |
| Floor | 0 | -- |
| Vent | 1 | -- |

| Model (H7-) | MBTUH |  | Dimensions (in.) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | A Length | F Mounting | G NPT | H NPT | K Flue Ø | T C/A Ø | W (Water) |
| 300A | 300 | 282 | 28-1/4 | 27-9/16 | 3/4 | 1-1/2 | 4 | 4 | 8-1/2 |
| 400A | 399 | 375 | 30-3/4 | 32-5/16 | 1 | 2 | 4 | 4 | 7 |
| 500A | 500 | 470 | 37-1/4 | 36-9/16 | 1 | 2 | 4 | 4 | 8-1/2 |
| 700A | 700 | 658 | 47-3/4 | 49-5/16 | 1-1/4 | 2 | 6 | 6 | 10-5/8 |
| 850A | 850 | 799 | 54-1/4 | 53-9/16 | 1-1/4 | 2 | 6 | 6 | 10-5/8 |

| RATES OF FLOW AND PRESSURE DROPS |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model (H7-) | 20ºF ∆T |  | 30ºF ∆T |  | 35ºF ∆T |  | Min Flow |  |  | Max Flow |  |  |
|  | GPM | ∆P** | GPM | ∆P** | GPM | ∆P | GPM | ∆P** | ∆T | GPM | ∆P** | ∆T |
| 300A | 28 | 17 | 19 | 8 | 16 | 6 | 14 | 5 | 39 | 36 | 28 | 16 |
| 400A | 38 | 18 | 25 | 7 | 21 | 5 | 19 | 4 | 39 | 47 | 29 | 16 |
| 500A | 47 | 16 | 31 | 7 | 27 | 5 | 24 | 4 | 39 | 56 | 23 | 17 |
| 700A | 66 | 30 | 44 | 13 | 38 | 9 | 34 | 7 | 39 | 70 | 34 | 19 |
| 850A* | 80 | 40* | 53 | 17 | 46 | 12 | 41 | 10 | 39 | 80 | 40 | 20 |

| Model (H7-) | Amps* | Foot- Print (ft2) | Ship Weight (lbs.) |
| --- | --- | --- | --- |
| 300A | 3 | 4.3 | 410 |
| 400A | 4 | 4.7 | 465 |
| 500A | 4 | 5.7 | 505 |
| 700A | 5 | 7.3 | 580 |
| 850A | 5 | 8.3 | 580 |

* Closed systems only

* Current draw is for heater only.

(Supply breaker must have delayed trip.)

** Connected plumbing pressure drops are not included.