### DIVISION 23 52 33.13

### STAINLESS STEEL HEATING BOILERS

- GENERAL

SUMMARY

Section includes condensing gas-fired, stainless steel hydronic heating boilers

Specifier Note:  Use as needed

Related Sections

Building Services Piping – Division 23 21 00

Breeching, Chimneys, and Stacks (Venting) – Division 23 51 00

HVAC Instrumentation and Controls – Division 23 09 00

Electrical – Division 23 09 33

REFERENCES

ANSI Z21.13/CSA 4.9

ASME, Section IV

2006 UMC, Section 1107.6

ANSI/ASHRAE 15-1994, Section 8.13.6

National Fuel Gas Code, ANSI Z223.1/NFPA 54

AHRI

NEC

ASME CSD-1, 2009

SUBMITTALS

Product data sheet (including dimensions, rated capacities, shipping weights, accessories)

Wiring diagram

Warranty information

Installation and operating instructions

QUALITY ASSURANCE

Regulatory Requirements

ANSI Z21.13/CSA 4.9

Local and national air quality regulations for low NOx boilers

Certifications

CSA

ASME, Section IV, H Stamp and National Board Listed

S.C.A.Q.M.D. Rule 1146.2 (<20 PPM NOx emissions @ 3% O2)

CSA Certified – AB 1953 & VLA 193 Low Lead Compliant

Heat Exchanger WARRANTY

Limited ten-year closed-system heat exchanger warranty

Limited twenty-five-year thermal shock warranty

- PRODUCTS

MANUFACTURER

Raypak, Inc.

Contact: 2151 Eastman Ave., Oxnard, CA 93030; Telephone: (805) 278-5300; 
Fax: (800) 872-9725; Web site: www.raypak.com

Product: XFyre™ condensing stainless steel hydronic heating boiler(s)

BOILERS

General

The boiler(s) shall be fired with                    gas at a rated input of                      BTU/hr.

The boiler(s) shall be CSA tested and certified with a minimum thermal efficiency of 94 percent at full fire.

The boiler(s) shall be ASME inspected and stamped and National Board registered for 160 PSIG maximum allowable working pressure and 210ºF maximum allowable temperature, complete with a Manufacturer's Data Report.

The boiler(s) shall have a floor loading of 95 lbs./square foot or less.

Primary Heat Exchanger

The primary heat exchanger shall be of a helically wound, multi-pass design and shall completely encircle the combustion chamber for maximum efficiency.

There shall be no banding material, gaskets or "O" rings in the header configuration. The heat exchanger is removable from the cabinet for replacement without removing the entire boiler assembly from the site. The stainless steel combustion chamber shall be designed to have a trough located on the bottom front and back section leading to the middle to ensure that condensation does not collect in the boiler.

The low water volume primary heat exchanger shall be explosion-proof on the water side and shall carry a twenty-five-year warranty against thermal shock.

The flue connection, combustion air opening, gas connection, electrical connections and condensate drain shall be located on the rear. Water connections shall be located on the left rear top of the unit.

Condensate Drain

The boiler(s) will feature a condensate float switch which will shut down the boiler(s) if the condensate drain is blocked.

Burner

The combustion chamber shall be of the sealed combustion type employing the Raypak high temperature metal fiber burner, mounted in a horizontal orientation.

The burner shall be a premix design and constructed of high grade Inconel and must be capable of firing at both a complete blue flame with maximum gas and air input as well as firing infrared when gas and air are reduced. The burner must be capable of firing at 100% of rated input when supplied with 4.0” WC of inlet gas pressure, so as to maintain service under heavy demand conditions; no exceptions.

The burner shall use a combustion air blower to precisely control the fuel/air mixture for maximum efficiency throughout the entire range of modulation. The combustion air blower shall operate for a pre-purge period before burner ignition and a post-purge period after burner operation to clear the combustion chamber.

The blower shall infinitely vary its output in response to a PWM signal supplied directly from the Versa IC modulating control, thereby electronically and precisely adjusting the volume of air and gas supplied for combustion. Minimum fire shall be 20 percent of rated input.

Ignition System

The boiler(s) shall be equipped with a 100 percent safety shutdown.

The ignition shall be spark ignition type with full flame rectification by the ignition source, with a four try-for-ignition sequence, to ensure consistent operation.

The igniter will be located above the burner to ensure easy ignition.

The Versa IC control module shall include an LCD display that indicates individual diagnostic faults.

A viewing port shall be provided, permitting visual observation of burner operation.

Gas Train

The boiler(s) shall have a firing/leak test valve and pressure test valve as required by CSD-1.

The boiler(s) shall have dual-seated main gas valve.

Gas control trains shall have a redundant safety shut-off feature, main gas regulation, and plugged pressure tapping to meet the requirements of ANSI Z21.13/CSA 4.9.

Boiler Control

The following safety controls shall be provided:

200#F High limit control with manual reset (maximum system setpoint 190#F)

Flow switch, mounted and wired

PSIG ASME pressure relief valve, piped by the installer to an approved drain (shipped loose)

Temperature and pressure gauge (shipped loose)

The boiler(s) shall be equipped with an integrated PID modulating temperature controller with LCD display that incorporates an adjustable energy-saving pump control relay and freeze protection and is factory mounted and wired to improve system efficiency; three water sensors are included (system sensor is loose).

The boiler(s) shall allow for 0-10 VDC input connection for remote building DDC system control of system temperature or firing rate and have a built-in “Cascade” function to sequence and rotate while maintaining modulation of up to four boilers without utilizing an external sequencer.

Firing Mode: Provide electronic modulating control of the gas input to the boiler.

Boiler Diagnostics

Provide monitoring of all safeties, internal/external interlocks with fault display by a 3-1/2” LCD display:

System status

Ignition failure

Condensate blockage

Blower speed error

Low 24VAC

Manual reset high limit

Auto reset high limit

Low Water Cut Off (LWCO) (optional)

Blocked vent

Low gas pressure switch (optional)

High gas pressure switch (optional)

Flow switch fault

Sensor failure

      - Inlet sensor (open or short)

      - Outlet sensor (open or short)

      - System sensor (open or short)

      - Air sensor (optional) (open or short)

      - DHW sensor (optional) (open or short)

High vent temperature

Internal control fault

ID Card fault

Cascade communication error

Cabinet

The corrosion-resistant galvanized-steel jackets shall be finished with a baked-on epoxy powder coat, which is suitable for outdoor installation, applied prior to assembly for complete coverage.

The boiler(s), if located on a combustible floor, shall not require a separate combustible floor base.

The boiler(s) shall connect both the combustion air and flue products through the back of the unit.

The heater shall have as standard an internal, combustion air filter rated to MERV 8 (>95% arrestance).

Boiler Pump – The boiler(s) shall be equipped with an optional factory-packaged pump system.

BOILER OPERATING CONTROLS

Each boiler shall have the ability to receive a 0 to 10 VDC signal from the Central Energy Management and Direct Digital Control System (EMCS) to vary the setpoint or control firing rate.. Each boiler shall have an alarm contact for connection to the central EMCS system.

Each boiler shall be equipped with Modbus communications compatibility with up to 146 points of data available.

The boiler(s) shall feature the integrated Versa IC modulating digital controller with 3 user selectable modes, mounted and wired.

Mode 1 = Hydronic, without indirect domestic hot water.

Mode 2 = Hydronic, with indirect domestic hot water plumbed into system loop piping

Mode 3 = Hydronic, with indirect domestic hot water plumbed into boiler loop plumbing

System sensor and optional air temperature sensor shall be shipped loose for field installation by installing contractor. Inlet/Outlet sensors are factory-installed.

Versa IC control system is capable of controlling up to 3 connected pumps.

Boiler pump

System pump

Indirect DHW pump

DIRECT VENT

The boiler(s) shall meet safety standards for direct vent equipment as noted by the 2006 Uniform Mechanical Code, section 1107.6, and ASHRAE 15-1994, section 8.13.6.

The boiler shall be capable of combined combustion air duct and vent lengths not to exceed 200 equivalent feet.

SOURCE QUALITY CONTROL

The boiler(s) shall be completely assembled, wired, and fire-tested prior to shipment from the factory.

The boiler(s) shall be furnished with the sales order, ASME Manufacturer’s Data Report(s), inspection sheet, wiring diagram, rating plate and Installation and Operating Manual.

- EXECUTION

INSTALLATION

Must comply with:

Local, state, provincial, and national codes, laws, regulations and ordinances

National Fuel Gas Code, ANSI Z223.1/NFPA 54 – latest edition

National Electrical Code, ANSI/NFPA 70 – latest edition

Standard for Controls and Safety Devices for Automatically Fired Boilers, ANSI/ASME CSD-1, when required

Canada only: CAN/CSA B149 Installation Code and CSA C22.1 CEC Part I

Manufacturer’s installation instructions, including required service clearances and venting guidelines

Manufacturer’s representative to verify proper and complete installation.

START-UP

Shall be performed by Raypak factory-trained personnel.

Test during operation and adjust if necessary:

Safeties

Operating controls

Static and full load gas supply pressure

Gas manifold and blower suction pressure

Combustion analysis

Submit copy of start-up report to Architect and Engineer.

training

Provide factory-authorized service representative to train maintenance personnel on procedures and schedules related to start-up, shut-down, troubleshooting, servicing, and preventive maintenance.

Schedule training at least seven days in advance.

END OF SECTION

# Text boxes

XFYRE™, TYPE H - MODELS 300A-850A
SUGGESTED SPECIFICATIONS

Catalog No.:	2000.81C

Effective:	04/05/13

Replaces:	04/21/11