# Hi Delta® - Type P

## Commercial Pool Heaters Models 992C-2342C

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Thermal Efficiency: 83.1%

- Versa IC® Controller with LCD Display

- Maximum Setpoint: 106°F (104°F Default)

- Maximum Outlet Temperature: 160°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal-Shock Proof Heat Exchanger

- Limited Five-Year Heat Exchanger Warranty

- Full Safety Diagnostics with Fault History

- PolyTuf Powder Coated Cabinet

- No Combustible Floor Shield Required

- Fan-Assisted

Standard “H” Bypass Shown

Patented Burner Security Blanket

- Ultra-Low NOx – SCAQMD 1146.2 Certified (992C – 2002C)

Proudly Assembled in the USA

Cascade Up To 4 Heaters – No External Sequencer Needed

#### Heat Exchanger

Brass Headers

ASME Inspected and HLW Stamped
160 PSIG Working Pressure

National Board Approved

Cupro-Nickel Finned Tubing

ASME Steel Tube Sheet

Silicone High-Temp O-Rings

125 PSIG ASME Pressure Relief Valve

Temperature and Pressure Gauge

Water Connections

Left – Standard

A-6 – Right

Bronze Pump, 1/2 HP, 120V, 60Hz

Non-ferrous Pool Bypass Assembly

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

Versa IC® Integrated Control

Cascade up to 4 Heaters

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try – Standard

- C-6 Single Try

Remote Flame Sensor

Fixed High Limit, Manual Reset 180°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Programmable Pump Time Delays

- Heater

- System

Enable/Disable

LCD Display; Status, Fault and Diagnostics

#### Controls – Cont.

Modbus RTU BMS Port (Up to 115K Baud Rate, See Cat. 5000.73)

- B-85 – BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86 – BMS Gateway – LonWorks

Cold Water Protection Function

- CWR Variable-Speed Pump

- Default H-Bypass

#### Gas Train

Combination Valves

On/Off Firing

Fuel

Natural Gas

Propane Gas (HD-5) (Excludes 2002C)

G-20  4” WC Nat. Supply Pressure

Design Certified ANSI Z21.56/CSA 4.7

#### Burner

Ultra-low NOx:
Less than 20 PPM

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

CSA Low Lead Certified ≤ .25% Lead

#### Venting

Vent Location

Top – Standard

D–14 Rear

Vent Termination Cap

D–11 Outdoor

D–15 Horizontal

Indoor, Vertical (by others)

Combustion Air

D–17 In-Line Filter Kit (TruSeal only)

D–16 Air Intake Elbow

#### Venting – Cont.

Extractor - Optional

By Others

#### Not Required

#### Options

C-6	Ignition Module, Manual Reset

D-21	TruSeal® Direct Vent

Left Side - Standard 
 Right Side - Optional

F-10	Low Water Cut-Off, 
Remote Probe

S-1	Low Gas Pressure Switch, Manual Reset

S-2		High Gas Pressure Switch, Manual Reset

X-1	SureRack® Kit (Lower Unit Requires Manifold Modification)

X-2	SureRack Add-On (Lower Unit Requires Manifold Modification)

Additional Options or Accessories

Multi-Heater Controllers

#### B-36	2 – 4 Heaters

#### B-37	5 – 10 Heaters

#### B-38	11 – 16 Heaters

#### B-39	EMS 4-20mA Remote Setpoint Module

#### B-62	BACnet MS/TP Interface

#### Hi Delta – Type P

#### Models 992C-1262C (H-Bypass Option)	Model

| Rate of Heat Exchanger Flow and Pressure Drop and Temperature Rise |  |  |  |
| --- | --- | --- | --- |
| Model | GPM | ΔP (ft.) | ΔT (ºF) |
| P 992C | 132 | 14.0 | 13 |
| P 1262C |  | 15.5 | 16 |

| Model | MBTUH |  | A Width | K | W | Amp. Draw (w/ Pump) | Pump HP | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output 83.1% |  |  |  |  |  |  |
| P 992C | 990 | 823 | 57-1/8 | 10 | 16-13/16 | <16 | 1/2 | 1000 |
| P 1262C | 1260 | 1047 | 68-1/2 | 12 | 20-9/16 |  |  | 1055 |

NOTES:	1. Dimensions are in inches.

2. Rates shown are for natural or propane gas, and elevations up to 4,500 feet.

For installation above 4,500 feet, please contact manufacturer.

#### Hi Delta – Type P

#### Models 992C-1262C (Cold Water Run Option)	Model

| Rate of Heat Exchanger Flow and Pressure Drop and Temperature Rise |  |  |  |
| --- | --- | --- | --- |
| Model | GPM | ΔP (ft.) | ΔT (ºF) |
| P 992C | 132 | 14.0 | 13 |
| P 1262C |  | 15.5 | 16 |

| Model | MBTUH |  | A Width | K | W | Amp. Draw (w/ Pump) | Pump HP | Injector Pump HP | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output 83.1% |  |  |  |  |  |  |  |
| P 992C | 990 | 823 | 57-1/8 | 10 | 1/3* | <16 | 1/2 | 1/3* | 1000 |
| P 1262C | 1260 | 1047 | 68-1/2 | 12 | 1/3* |  |  |  | 1055 |

NOTES:	1. Dimensions are in inches.

2. Rates shown are for natural or propane gas, and elevations up to 4,500 feet.

For installation above 4,500 feet, please contact manufacturer.

*Separate 120 VAC or 240 VAC 1Ø power required for Cold Water Run Option.

Injector shipped loose for field installation at bypass inlet.

#### Hi Delta – Type P

#### Models 1532C-2342C (H-Bypass Option)	Model

| Rate of Heat Exchanger Flow and Pressure Drop and Temperature Rise |  |  |  |
| --- | --- | --- | --- |
| Model | GPM | ΔP (ft.) | ΔT (ºF) |
| P 1532C | 132 | 16.5 | 20 |
| P 1802C |  | 18.3 | 23 |
| P 2002C |  | 19.0 | 26 |
| P 2072C |  | 19.0 | 27 |
| P 2342C |  | 21.4 | 30 |

| Model | MBTUH |  | A Width | K | W | Amp. Draw |  | Pump HP | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output 83.1% |  |  |  | Heater | Pump |  |  |
| P 1532C | 1530 | 1271 | 79-7/8 | 12 | 24-3/8 | <12 | 11 | 3/4 | 1225 |
| P 1802C | 1800 | 1496 | 91-1/8 | 14 | 28-1/8 |  | 11 | 3/4 | 1350 |
| P 2002C | 1999 | 1661 | 102-1/2 | 14 | 31-15/16 |  | 14** | 1 | 1450 |
| P 2072C | 2070 | 1720 | 102-1/2 | 14 | 31-15/16 |  | 14** | 1 | 1450 |
| P 2342C | 2070 | 1945 | 113-7/8 | 16 | 35-11/16 |  | 21** | 1-1/2 | 1520 |

NOTES:	1. Dimensions are in inches.

2. Rates shown are for natural or propane gas, and elevations up to 4,500 feet.

For installation above 4,500 feet, please contact manufacturer.

** Requires separate circuit breaker

#### Hi Delta – Type P

#### Models 1532C-2342C (Cold Water Run Option)	Model

| Rate of Heat Exchanger Flow and Pressure Drop and Temperature Rise |  |  |  |
| --- | --- | --- | --- |
| Model | GPM | ΔP (ft.) | ΔT (ºF) |
| P 1532C | 132 | 16.5 | 20 |
| P 1802C |  | 18.3 | 23 |
| P 2002C |  | 19.0 | 26 |
| P 2072C |  | 19.0 | 27 |
| P 2342C |  | 21.4 | 30 |

| Model | MBTUH |  | A Width | K | W | Amp. Draw |  | Injector Pump HP | Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output 83.1% |  |  |  | Heater | Pump |  |  |
| P 1532C | 1530 | 1271 | 79-7/8 | 12 | 24-3/8 | <12 | 11 | 1/3 | 1225 |
| P 1802C | 1800 | 1496 | 91-1/8 | 14 | 28-1/8 |  | 11 | 1/3 | 1350 |
| P 2002C | 1999 | 1661 | 102-1/2 | 14 | 31-15/16 |  | 14** | 3/4 | 1450 |
| P 2072C | 2070 | 1720 | 102-1/2 | 14 | 31-15/16 |  | 14** | 3/4 | 1450 |
| P 2342C | 2070 | 1945 | 113-7/8 | 16 | 35-11/16 |  | 21** | 3/4 | 1520 |

NOTES:	1. Dimensions are in inches.

2. Rates shown are for natural or propane gas, and elevations up to 4,500 feet.

For installation above 4,500 feet, please contact manufacturer.

** Requires separate circuit breaker

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com