## INDEX PAGE
|  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  | SUBMITTAL DATA SHEET
|  | 3885 Crestwood Parkway / Suite 500 |  |  | New Low Profile Unit Cooler
|  | Duluth, GA 30096 |  |  | Electric Defrost
|  | (P) 800-288-9488 / (F) 256-259-7478 |  |  |  | For Record Only
|  | http://Witt.htpgusa.com |  |  |  | For Approval
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
| 1-FAN / 6 FPI |  | WL6E035 | 1-FAN / 4 FPI |  | WL4E027
|  |  | WL6E042 |  |  | WL4E032
|  |  | WL6E049 |  |  | WL4E038
| 2-FAN / 6 FPI |  | WL6E066 | 2-FAN / 4 FPI |  | WL4E051
|  |  | WL6E077 |  |  | WL4E064
|  |  | WL6E090 |  |  | WL4E080
|  |  | WL6E105 | 3-FAN / 4 FPI |  | WL4E094
| 3-FAN / 6 FPI |  | WL6E121 |  |  | WL4E110
|  |  | WL6E142 | 4-FAN / 4 FPI |  | WL4E125
| 4-FAN / 6 FPI |  | WL6E162 |  |  | WL4E141
|  |  | WL6E182 | 5-FAN / 4FPI |  | WL4E155
| 5-FAN / 6FPI |  | WL6E200 | 6-FAN / 4 FPI |  | WL4E195
| 6-FAN / 6 FPI |  | WL6E244 |  |  | WL4E230
WL6E281

## 1-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Electric Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://Witt.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 11:09
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20 F |  | -20 F |  |  | Fans | Diameter
| WL6E035 |  | 3500 |  | 4000 |  |  | 1 | 12' | 800 | 25'
| WL6E042 |  | 4200 |  | 4900 |  |  | 1 | 12" | 785 | 25'
| WL6E049 |  | 4900 |  | 5600 |  |  | 1 | 12" | 775 | 25'
| WL4E027 |  | 2700 |  | 3100 |  |  | 1 | 12" | 800 | 25'
| WL4E032 |  | 3200 |  | 3800 |  |  | 1 | 12" | 785 | 25'
| WL4E038 |  | 3800 |  | 4400 |  |  | 1 | 12" | 775 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight Lbs. | 230v or 460v | 230v or 460v
|  | WL6E035 |  | 6 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 0.8 | 41 | 15 | 20
|  | WL6E042 |  | 6 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 1.2 | 44 | 15 | 20
|  | WL6E049 |  | 6 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 1.6 | 47 | 15 | 20
|  | WL4E027 |  | 4 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 0.8 | 40 | 15 | 20
|  | WL4E032 |  | 4 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 1 | 42 | 15 | 20
|  | WL4E0638 |  | 4 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 1.2 | 46 | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | Heater | Heater | PSC Mtr | EC Mtr | Total Motor Amps
Code |  |  |  | Amps | Watts | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
D | 208/230 | 1 | 60 | 4.9 | 1125 | 0.5 | 0.5 | 0.5 | 0.5
E | 208/230 | 3 | 60 | 2.9 | 1125 | 0.5 | 0.5 | 0.5 | 0.5
F | 460 | 1 | 60 | 2.5 | 1125 | 0.4 | N/A | 0.4 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
Witt New Low Profile Unit Cooler Elec. Subm.
1 - FAN
Electric
Defrost
SUCTION
Liquid
(2) Back & (3) Top
L
6
D
E
B
W
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
Witt
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 2-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Electric Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://Witt.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 11:09
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20 F |  | -20 F |  |  | Fans | Diameter
| WL6E066 |  | 6600 |  | 7600 |  |  | 2 | 12' | 1600 | 25'
| WL6E077 |  | 7700 |  | 8800 |  |  | 2 | 12" | 1570 | 25'
| WL6E090 |  | 9000 |  | 10600 |  |  | 2 | 12" | 1550 | 25'
| WL6E105 |  | 10500 |  | 12400 |  |  | 2 | 12" | 1550 | 25'
| WL4E051 |  | 5100 |  | 5900 |  |  | 2 | 12" | 1600 | 25'
| WL4E064 |  | 6400 |  | 7300 |  |  | 2 | 12" | 1570 | 25'
| WL4E080 |  | 8000 |  | 9500 |  |  | 2 | 12" | 1550 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight Lbs. | 230v or 460v | 230v or 460v
|  | WL6E066 |  | 6 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 1.3 | 52 | 15 | 20
|  | WL6E077 |  | 6 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 2 | 55 | 15 | 20
|  | WL4E090 |  | 6 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 3 | 58 | 15 | 20
|  | WL6E105 |  | 6 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 3.2 | 62 | 15 | 20
|  | WL4E051 |  | 4 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 1.6 | 50 | 15 | 20
|  | WL4E064 |  | 4 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 2.2 | 52 | 15 | 20
|  | WL4E080 |  | 4 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 3 | 55 | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | Heater | Heater | PSC Mtr | EC Mtr | Total Motor Amps
Code |  |  |  | Amps | Watts | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
D | 208/230 | 1 | 60 | 9.8 | 2250 | 0.5 | 0.5 | 1 | 1
E | 208/230 | 3 | 60 | 5.7 | 2250 | 0.5 | 0.5 | 1 | 1
F | 460 | 1 | 60 | 4.9 | 2250 | 0.4 | N/A | 0.8 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
Witt New Low Profile Unit Cooler Elec. Subm.
2 - FAN
Electric
Defrost
SUCTION
Liquid
(2) Back & (3) Top
L
6
D
E
B
W
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
Witt
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 3-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Electric Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://Witt.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 11:09
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20 F |  | -20 F |  |  | Fans | Diameter
| WL6E121 |  | 12100 |  | 14200 |  |  | 3 | 12' | 2355 | 25'
| WL6E142 |  | 14200 |  | 16600 |  |  | 3 | 12" | 2325 | 25'
| WL4E094 |  | 9400 |  | 11000 |  |  | 3 | 12" | 2355 | 25'
| WL4E110 |  | 11000 |  | 12800 |  |  | 3 | 12" | 2325 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight | 230v or 460v | 230v or 460v
|  | WL6E121 |  | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 3.2 | 78 Lb's | 15 | 20
|  | WL6E142 |  | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.3 | 85 Lb's | 15 | 20
|  | WL4E094 |  | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 3.2 | 79 Lb's | 15 | 20
|  | WL4E110 |  | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.3 | 84 Lb's | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | Heater | Heater | PSC Mtr | EC Mtr | Total Motor Amps
Code |  |  |  | Amps | Watts | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
D | 208/230 | 1 | 60 | 14.3 | 3300 | 0.5 | 0.5 | 1.5 | 1.5
E | 208/230 | 3 | 60 | 8.3 | 3300 | 0.5 | 0.5 | 1.5 | 1.5
F | 460 | 1 | 60 | 7.2 | 3300 | 0.4 | N/A | 1.2 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
Witt New Low Profile Unit Cooler Elec. Subm.
SUCTION
3 - FAN
Electric
Defrost
Liquid
(2) Back & (3) Top
L
6
D
E
B
W
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
Witt
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 4-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Electric Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://Witt.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 11:09
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20 F |  | -20 F |  |  | Fans | Diameter
| WL6E162 |  | 16200 |  | 18700 |  |  | 4 | 12' | 3140 | 25'
| WL6E182 |  | 18200 |  | 21000 |  |  | 4 | 12" | 3100 | 25'
| WL4E125 |  | 12500 |  | 14400 |  |  | 4 | 12" | 3140 | 25'
| WL4E141 |  | 14100 |  | 16300 |  |  | 4 | 12" | 3100 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight | 230v or 460v | 230v or 460v
|  | WL6E162 |  | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.3 | 124 Lb's | 15 | 20
|  | WL6E182 |  | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 5.7 | 147 Lb's | 15 | 20
|  | WL4E125 |  | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 3.2 | 124 Lb's | 15 | 20
|  | WL4E141 |  | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.3 | 144 Lb's | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | Heater | Heater | PSC Mtr | EC Mtr | Total Motor Amps
Code |  |  |  | Amps | Watts | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
D | 208/230 | 1 | 60 | 19.2 | 4425 | 0.5 | 0.5 | 2 | 2
E | 208/230 | 3 | 60 | 11.1 | 4425 | 0.5 | 0.5 | 2 | 2
F | 460 | 1 | 60 | 9.6 | 4425 | 0.4 | N/A | 1.6 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
Witt New Low Profile Unit Cooler Elec. Subm.
SUCTION
Liquid
(2) Back & (3) Top
4 - FAN
Electric
Defrost
L
6
D
E
B
W
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
Witt
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 5-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Electric Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://Witt.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 11:09
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20 F |  | -20 F |  |  | Fans | Diameter
| WL6E200 |  | 20000 |  | 22800 |  |  | 5 | 12' | 3925 | 25'
| WL4E155 |  | 15500 |  | 17700 |  |  | 5 | 12" | 3925 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight | 230v or 460v | 230v or 460v
|  | WL6E200 |  | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 5.3 | 195 Lb's | 15 | 20
|  | WL4E155 |  | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 5.3 | 191 Lb's | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | Heater | Heater | PSC Mtr | EC Mtr | Total Motor Amps
Code |  |  |  | Amps | Watts | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
D | 208/230 | 1 | 60 | 24.1 | 5550 | 0.5 | 0.5 | 2.5 | 2.5
E | 208/230 | 3 | 60 | 14 | 5550 | 0.5 | 0.5 | 2.5 | 2.5
F | 460 | 1 | 60 | 12 | 5550 | 0.4 | N/A | 2 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
Witt New Low Profile Unit Cooler Elec. Subm.
SUCTION
5 - FAN
Electric
Defrost
Liquid
(2) Back & (3) Top
L
6
D
E
B
W
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
Witt
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 6-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Electric Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://Witt.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 11:09
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20 F |  | -20 F |  |  | Fans | Diameter
| WL6E244 |  | 24400 |  | 27900 |  |  | 6 | 12' | 4710 | 25'
| WL6E281 |  | 28100 |  | 33000 |  |  | 6 | 12" | 4650 | 25'
| WL4E195 |  | 19500 |  | 22300 |  |  | 6 | 12" | 4710 | 25'
| WL4E230 |  | 23000 |  | 27000 |  |  | 6 | 12" | 4650 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight | 230v or 460v | 230v or 460v
|  | WL6E244 |  | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.3 | 238 Lb's | 15 | 20
|  | WL6E281 |  | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 5.7 | 262 Lb's | 15 | 20
|  | WL4E195 |  | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 3.2 | 257 Lb's | 15 | 20
|  | WL4E230 |  | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.3 | 262 Lb's | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | Heater | Heater | PSC Mtr | EC Mtr | Total Motor Amps
Code |  |  |  | Amps | Watts | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
D | 208/230 | 1 | 60 | 29 | 6675 | 0.5 | 0.5 | 3 | 3
E | 208/230 | 3 | 60 | 16.8 | 6675 | 0.5 | 0.5 | 3 | 3
F | 460 | 1 | 60 | 14.5 | 6675 | 0.4 | N/A | 2.4 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
Witt New Low Profile Unit Cooler Elec. Subm.
SUCTION
Liquid
(2) Back & (3) Top
6 - FAN
Electric
Defrost
L
6
D
E
B
W
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
Witt
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## Model Nomenclature
W
L
6
E
042
D
E
A
B
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
WITT
FIns Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Singel Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuratidescriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625