## W_SUB_INDEX
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  | SUBMITTAL DATA INDEX
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  | Medium Temp Hermetic
|  |  | Duluth, GA 30096 |  |  | W - Series Models WBH / WFH
|  |  | (P) 800-288-9488 / (F) 256-259-7478 |  |  | Next Generation
|  |  | http://witt.htpgusa.com |  |  | Air Cooled Condensing Unit
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
| REFRIGERANT | VOLTS / PHASE / HERTZ
|  | 208/230/1/60 |  | 208/230/3/60 | 460/3/60
| R404A | W*H055E44-DA |  | N/A | N/A
|  | W*H080E44-DA |  | N/A | N/A
|  | W*H090E44-DA |  | N/A | N/A
|  | W*H100E44-DA |  | W*H100E44-EA | N/A
|  | W*H125E44-DA |  | W*H125E44-EA | N/A
|  | W*H150E44-DA |  | W*H150E44-EA | N/A
|  | W*H200E44-DA |  | W*H200E44-EA | N/A
|  | W*H250E44-DA |  | W*H250E44-EA | W*H250E44-GA
|  | W*H300E44-DA |  | W*H300E44-EA | W*H300E44-GA
|  | W*H325E44-DA |  | W*H325E44-EA | W*H325E44-GA
NOTE | * Designates model style; "B" is non-flooded model / "F" is flooded model ("flood" = low ambient head press control valve)
3720
W_SUB_INDEX_1115-A

## W_H055E44-DA-R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 6660 | 6020 | 5420 | 4350 | 3850 | 3390
|  |  | +95 Deg F |  | 6350 | 5740 | 5170 | 4130 | 3660 | 3210
|  |  | +100 Deg F |  | 6030 | 5450 | 4900 | 3910 | 3460 | 3030
|  |  | +105 Deg F |  | 5710 | 5150 | 4640 | 3690 | 3260 | 2840
|  |  | +110 Deg F |  | 5380 | 4860 | 4360 | 3460 | 3050 | 2660
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST45C1E |  | 0.5 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 137 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 4.6 | 26.5 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H080E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 8270 | 7410 | 6610 | 5180 | 4540 | 3960
|  |  | +95 Deg F |  | 7860 | 7040 | 6270 | 4890 | 4280 | 3720
|  |  | +100 Deg F |  | 7460 | 6670 | 5930 | 4610 | 4020 | 3490
|  |  | +105 Deg F |  | 7050 | 6310 | 5600 | 4330 | 3770 | 3260
|  |  | +110 Deg F |  | 6660 | 5950 | 5270 | 4070 | 3530 | 3040
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST55C1E |  | 0.5 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 140 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 6.1 | 33.7 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H090E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 9930 | 9080 | 8260 | 6690 | 5950 | 5250
|  |  | +95 Deg F |  | 9470 | 8650 | 7860 | 6360 | 5650 | 4950
|  |  | +100 Deg F |  | 9010 | 8220 | 7460 | 6020 | 5340 | 4700
|  |  | +105 Deg F |  | 8540 | 7790 | 7070 | 5690 | 5040 | 4420
|  |  | +110 Deg F |  | 8060 | 7350 | 6660 | 5360 | 4740 | 4150
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST64C1E |  | 0.75 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 144 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 8.1 | 43 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H100E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 10590 | 9570 | 8610 | 6820 | 6010 | 5250
|  |  | +95 Deg F |  | 10090 | 9110 | 8190 | 6480 | 5700 | 4970
|  |  | +100 Deg F |  | 9580 | 8650 | 7770 | 6130 | 5380 | 4690
|  |  | +105 Deg F |  | 9070 | 8180 | 7340 | 5780 | 5060 | 4390
|  |  | +110 Deg F |  | 8550 | 7700 | 6900 | 5420 | 4730 | 4100
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST70C1E |  | 0.75 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 150 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 6.9 | 46 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H100E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 10590 | 9570 | 8610 | 6820 | 6010 | 5250
|  |  | +95 Deg F |  | 10090 | 9110 | 8190 | 6480 | 5700 | 4970
|  |  | +100 Deg F |  | 9580 | 8650 | 7770 | 6130 | 5380 | 4690
|  |  | +105 Deg F |  | 9070 | 8180 | 7340 | 5780 | 5060 | 4390
|  |  | +110 Deg F |  | 8550 | 7700 | 6900 | 5420 | 4730 | 4100
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST70C1E |  | 0.75 | 1 | 5.9 Lb's | 11 Lb's | 1.63 Lb's | 2.73 Lb's | 3/8" | 5/8" | 68 | 150 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 4.9 | 36 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H125E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 14260 | 13080 | 11910 | 9690 | 8640 | 7640
|  |  | +95 Deg F |  | 13620 | 12470 | 11350 | 9200 | 8190 | 7230
|  |  | +100 Deg F |  | 12960 | 11860 | 10780 | 8710 | 7740 | 6810
|  |  | +105 Deg F |  | 12290 | 11240 | 10200 | 8210 | 7280 | 6390
|  |  | +110 Deg F |  | 11630 | 10610 | 9610 | 7710 | 6810 | 5960
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST97C1E |  | 1 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.87 Lb's | 1/2" | 7/8" | 72 | 175 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9 | 51 | 1 | 4 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H125E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 14,260 | 13080 | 11910 | 9690 | 8640 | 7640
|  |  | +95 Deg F |  | 13,620 | 12470 | 11350 | 9200 | 8190 | 7230
|  |  | +100 Deg F |  | 12,960 | 11860 | 10780 | 8710 | 7740 | 6810
|  |  | +105 Deg F |  | 12,290 | 11240 | 10200 | 8210 | 7280 | 6390
|  |  | +110 Deg F |  | 11630 | 10610 | 9610 | 7710 | 6810 | 5960
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | RST97C1E |  | 1 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.87 Lb's | 1/2" | 7/8" | 72 | 175 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 5.4 | 36 | 1 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H150E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 16,270 | 14720 | 13190 | 10260 | 8870 | 7530
|  |  | +95 Deg F |  | 15,280 | 13810 | 12340 | 9530 | 8200 | 6920
|  |  | +100 Deg F |  | 14,320 | 12910 | 11490 | 8810 | 7540 | 6320
|  |  | +105 Deg F |  | 13,340 | 11990 | 10650 | 8090 | 6880 | 5720
|  |  | +110 Deg F |  | 12380 | 11090 | 9820 | 7380 | 6230 | 5120
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS10K6E |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.87 Lb's | 1/2" | 7/8" | 72 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9.8 | 56 | 1 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H150E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 16270 | 14720 | 13190 | 10260 | 8870 | 7530
|  |  | +95 Deg F |  | 15280 | 13810 | 12340 | 9530 | 8200 | 6920
|  |  | +100 Deg F |  | 14320 | 12910 | 11490 | 8810 | 7540 | 6320
|  |  | +105 Deg F |  | 13340 | 11990 | 10650 | 8090 | 6880 | 5720
|  |  | +110 Deg F |  | 11090 | 9820 | 9820 | 7380 | 6230 | 5120
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS10K6E |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.87 Lb's | 1/2" | 7/8" | 72 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 6.7 | 51 | 1 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H150E44_GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 16270 | 14720 | 13190 | 10260 | 8870 | 7530
|  |  | +95 Deg F |  | 15280 | 13810 | 12340 | 9530 | 8200 | 6920
|  |  | +100 Deg F |  | 14320 | 12910 | 11490 | 8810 | 7540 | 6320
|  |  | +105 Deg F |  | 13340 | 11990 | 10650 | 8090 | 6880 | 5720
|  |  | +110 Deg F |  | 11090 | 9820 | 9820 | 7380 | 6230 | 5120
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS10K6E |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.87 Lb's | 1/2" | 7/8" | 72 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.2 | 25 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H200E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 18960 | 16960 | 15070 | 11650 | 10100 | 8640
|  |  | +95 Deg F |  | 17870 | 15950 | 14140 | 10850 | 9360 | 7970
|  |  | +100 Deg F |  | 16800 | 14950 | 13210 | 10050 | 8630 | 7300
|  |  | +105 Deg F |  | 15720 | 13950 | 12280 | 9270 | 7910 | 6650
|  |  | +110 Deg F |  | 14610 | 12940 | 11360 | 8490 | 7200 | 6000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS12K6E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.87 Lb's | 1/2" | 7/8" | 72 | 205 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9.8 | 56 | 1 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H200E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 18960 | 16960 | 15070 | 11650 | 10100 | 8640
|  |  | +95 Deg F |  | 17870 | 15950 | 14140 | 10850 | 9360 | 7970
|  |  | +100 Deg F |  | 16800 | 14950 | 13210 | 10050 | 8630 | 7300
|  |  | +105 Deg F |  | 15720 | 13950 | 12280 | 9270 | 7910 | 6650
|  |  | +110 Deg F |  | 14610 | 12940 | 11360 | 8490 | 7200 | 6000
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS12K6E |  | 2 | 2 | 11 Lb's | 13.6 Lb's | 3.1 Lb's | 4.87 Lb's | 1/2" | 7/8" | 72 | 205 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 6.7 | 51 | 1 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H250E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 22170 | 20230 | 18300 | 14510 | 12700 | 10980
|  |  | +95 Deg F |  | 20940 | 19070 | 17230 | 13620 | 11890 | 10240
|  |  | +100 Deg F |  | 19700 | 17920 | 16160 | 12730 | 11080 | 9510
|  |  | +105 Deg F |  | 18440 | 16750 | 15090 | 11830 | 10270 | 8780
|  |  | +110 Deg F |  | 17200 | 15600 | 14030 | 10940 | 9460 | 8050
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS14K6E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 212 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 11.2 | 61 | 1 | 10 | 28 | 16 | 25 | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H250E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 22170 | 20230 | 18300 | 14510 | 12700 | 10980
|  |  | +95 Deg F |  | 20940 | 19070 | 17230 | 13620 | 11890 | 10240
|  |  | +100 Deg F |  | 19700 | 17920 | 16160 | 12730 | 11080 | 9510
|  |  | +105 Deg F |  | 18440 | 16750 | 15090 | 11830 | 10270 | 8780
|  |  | +110 Deg F |  | 17200 | 15600 | 14030 | 10940 | 9460 | 8050
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS14K6E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 212 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.2 | 55 | 1 | 10 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H250E44-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 22170 | 20230 | 18300 | 14510 | 12700 | 10980
|  |  | +95 Deg F |  | 20,940 | 19070 | 17230 | 13620 | 11890 | 10240
|  |  | +100 Deg F |  | 19,700 | 17920 | 16160 | 12730 | 11080 | 9510
|  |  | +105 Deg F |  | 18,440 | 16750 | 15090 | 11830 | 10270 | 8780
|  |  | +110 Deg F |  | 17200 | 15600 | 14030 | 10940 | 9460 | 8050
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS14K6E |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 212 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.2 | 28 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H300E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 27060 | 24730 | 22400 | 17760 | 15500 | 13300
|  |  | +95 Deg F |  | 25490 | 23260 | 21020 | 16560 | 14400 | 12310
|  |  | +100 Deg F |  | 24000 | 21820 | 19650 | 15390 | 13320 | 11330
|  |  | +105 Deg F |  | 22420 | 20370 | 18320 | 14230 | 12270 | 10380
|  |  | +110 Deg F |  | 20890 | 18940 | 16990 | 13110 | 11240 | 9460
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS18K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 73 | 228 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.4 | 82 | 1 | 10 | 28 | 20 | 30 | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H300E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 27060 | 24730 | 22400 | 17760 | 15500 | 13300
|  |  | +95 Deg F |  | 25490 | 23260 | 21020 | 16560 | 14400 | 12310
|  |  | +100 Deg F |  | 24000 | 21820 | 19650 | 15390 | 13320 | 11330
|  |  | +105 Deg F |  | 22420 | 20370 | 18320 | 14230 | 12270 | 10380
|  |  | +110 Deg F |  | 20890 | 18940 | 16990 | 13110 | 11240 | 9460
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS18K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 73 | 228 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.4 | 65.5 | 1 | 10 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H300E44-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 27060 | 24730 | 22400 | 17760 | 15500 | 13300
|  |  | +95 Deg F |  | 25490 | 23260 | 21020 | 16560 | 14400 | 12310
|  |  | +100 Deg F |  | 24000 | 21820 | 19650 | 15390 | 13320 | 11330
|  |  | +105 Deg F |  | 22420 | 20370 | 18320 | 14230 | 12270 | 10380
|  |  | +110 Deg F |  | 20890 | 18940 | 16990 | 13110 | 11240 | 9460
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS18K6E |  | 3 | 2 | 13.6 Lb's | 20.9 Lb's | 3.8 Lb's | 7.83 Lb's | 1/2" | 7/8" | 73 | 228 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.2 | 33 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H325E44-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 35720 | 31530 | 27770 | 21320 | 18560 | 16050
|  |  | +95 Deg F |  | 33580 | 29590 | 25970 | 19800 | 17170 | 14770
|  |  | +100 Deg F |  | 31510 | 27670 | 24210 | 18310 | 15790 | 13510
|  |  | +105 Deg F |  | 29440 | 25780 | 22470 | 16840 | 14440 | 12260
|  |  | +110 Deg F |  | 27470 | 23920 | 20780 | 15410 | 13130 | 11050
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS20K6E |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11 Lb's | 5/8" | 1-1/8" | 73 | 246 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16.7 | 96 | 3.1 | 12 | 30 | 24.9 | 40 | 38.5 | 50
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H325E44-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 35720 | 31530 | 27770 | 21320 | 18560 | 16050
|  |  | +95 Deg F |  | 33580 | 29590 | 25970 | 19800 | 17170 | 14770
|  |  | +100 Deg F |  | 31510 | 27670 | 24210 | 18310 | 15790 | 13510
|  |  | +105 Deg F |  | 29440 | 25780 | 22470 | 16840 | 14440 | 12260
|  |  | +110 Deg F |  | 27470 | 23920 | 20780 | 15410 | 13130 | 11050
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS20K6E |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11 Lb's | 5/8" | 1-1/8" | 73 | 246 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 10.2 | 75 | 3.1 | 12 | 25 | 16.8 | 25 | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A

## W_H325E44-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | W Series - Model WBH / WFH
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://witt.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-02-15 08:05
|  |  | Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
|  |  | Ambient |  | Saturated Suction Temperature (SST)
|  |  | Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F
|  |  | +90 Deg F |  | 35720 | 31530 | 27770 | 21320 | 18560 | 16050
|  |  | +95 Deg F |  | 33580 | 29590 | 25970 | 19800 | 17170 | 14770
|  |  | +100 Deg F |  | 31510 | 27670 | 24210 | 18310 | 15790 | 13510
|  |  | +105 Deg F |  | 29440 | 25780 | 22470 | 16840 | 14440 | 12260
|  |  | +110 Deg F |  | 27470 | 23920 | 20780 | 15410 | 13130 | 11050
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Hermetic |  | CS20K6E |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 7.8 Lb's | 11 Lb's | 5/8" | 1-1/8" | 73 | 246 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.6 | 40 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model WFH) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
W_SBMTL_1115-A