Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

100% Factory Fire Tested

Efficiency: 84%

Maximum Outlet Temperature: 230°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-Year Thermal Shock Warranty

Limited Ten-Year Closed-System Heat Exchanger 
Warranty

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-Assisted

Patented Burner Security Blanket

Heat Exchanger

H Stamp

Headers

Glass-Lined Cast Iron – Standard

Bronze – Option A-1

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp O-Rings

ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

Right – Option A-6

#### Controls

120V, 60Hz, 1 Phase Power 
Supply

120/24V 60Hz Transformer

100% Shut-Off/Lockout

Hot Surface Ignition

Remote Flame Sensor

High Limit Control, Manual Reset

On/Off Power Switch

Manual Shut-Off, Front-Mounted Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Pump Time Delay Relay

Status Display Lights

#### Gas Train

Manual Gas Shut-Off Valve(s)

Combination Valves

Low Gas Pressure Switch, Manual

Firing Stages

2-Stage: Model 989B

3-Stage: Model 1259B

4-Stage: Models 1529B-2339B

Fuel

Natural Gas

Propane Gas

Design Certified - ANSI Z21.13/CSA 4.9

#### Burner

Ultra-Low NOx: Less than 
20 PPM

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

CSA Low Lead Certified ≤ .25 Pb

#### Venting

Vent Location

Top, Outdoor – Standard

Top, Indoor – Option D-20

Rear – Option D-14

Vent Termination Cap

Outdoor D-11

Indoor, Horizontal D-15

Indoor, Vertical (by others)

Extractor – Optional

By others

Not required

#### Temperature Controls

B-6	Aquastat, 2-Stage (100-200ºF)

B-__	TempTracker Digital Controller, 2-Stage (Loose)

B-__	TempTracker Digital Controller, 4-Stage (Loose)

B-__	TempTracker Mod+ Hybrid (2-16 Boilers)

B-60	Stage Interface

#### Options

C-6	Ignition Module, Manual Reset

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump:       HP, 120V, 
1(, 60Hz

Cast Iron	 Bronze
 Mounted	 Loose

Front	 Rear

P-  	Cold Water Start 
(See 2000.48)

S-2	High Gas Pressure Switch, Manual

X-1	SureRack™ Kit

X-2	SureRack Add-on

#### Regulatory Agency Requirements

#### Delta Limited – Type H

Models 989B-2339B	Model

# Text boxes

# Delta Limited™ - Type H

## Space Heating/Hot Water Boiler Models 989B-2339B

Shown with outdoor 
air inlet and pump covers

Proudly Assembled in the USA

Delta Limited models not approved for use in California

For Metric information, see Catalog

For Metric information, see Catalog

RATES OF FLOW AND PRESSURE DROPS

|  | 20°F ∆T | 30°F ∆T | Min. Flow | Max. Flow |
| --- | --- | --- | --- | --- |
| Model | GPM | ∆P (ft) | GPM | ∆P (ft) | GPM | ∆P (ft) | ∆T | GPM | ∆P (ft) | ∆T |
| 989B | 84 | 5.6 | 56 | 2.5 | 42 | 1.5 | 40 | 132 | 14.0 | 13 |
| 1259B | 107 | 10.0 | 71 | 4.5 | 53 | 2.6 | 40 | 132 | 15.5 | 16 |
| 1529B | 130 | 16.0 | 86 | 7.1 | 65 | 4.1 | 40 | 132 | 16.5 | 20 |
| 1799B | N/A | N/A | 102 | 10.8 | 76 | 6.0 | 40 | 132 | 18.0 | 23 |
| 1999B | N/A | N/A | 113 | 14.0 | 85 | 8.1 | 40 | 132 | 19.5 | 26 |
| 2069B | N/A | N/A | 117 | 15.0 | 88 | 8.7 | 40 | 132 | 19.5 | 27 |
| 2339B | N/A | N/A | 132 | 21.0 | 99 | 12.0 | 40 | 132 | 21.0 | 30 |

Basis is 40°F ∆T for minimum flow, 132 GPM for maximum flow.

NOTE:
Pump location varies based on model selected

Raypak, Inc. ( 2151 Eastman Avenue, Oxnard, CA  93030 ( (805) 278-5300 ( Fax (800) 872-9725 ( www.raypak.com

SPECIFICATIONS

|  |  |  |  |  |  |  |  |  | Approx. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH | Firing | A | H | K | W | Amp. | Shipping |
| Model | Input | Output | Stages | Width | NPT |  |  | Draw* | Wt. (Lbs.) |
| 989B | 990 | 832 | 2 | 57-1/8 | 2-1/2 | 10 | 16-13/16 | < 12 | 900 |
| 1259B | 1260 | 1058 | 3 | 68-1/2 | 2-1/2 | 12 | 20-9/16 | < 12 | 1010 |
| 1529B | 1530 | 1285 | 4 | 79-7/8 | 2-1/2 | 12 | 24-3/8 | < 12 | 1225 |
| 1799B | 1800 | 1512 | 4 | 91-1/8 | 2-1/2 | 14 | 28-1/8 | < 12 | 1350 |
| 1999B** | 1999 | 1679 | 4 | 102-1/2 | 2-1/2 | 14 | 31-15/16 | < 12 | 1450 |
| 2069B | 2070 | 1739 | 4 | 102-1/2 | 2-1/2 | 14 | 31-15/16 | < 12 | 1450 |
| 2339B | 2340 | 1966 | 4 | 113-7/8 | 2-1/2 | 16 | 35-11/16 | < 12 | 1520 |

* Pump not included

** Natural Gas Only

Dimensions are in inches.

Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

Recommended natural gas supply pressure is 7 – 10.5” WC. Recommended propane gas supply pressure is 
11 - 13” WC.