## R_SUB_INDEX
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  | SUBMITTAL DATA INDEX
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  | Extended Medium Temp Scroll
|  |  | Duluth, GA 30096 |  |  | R - Series Models RBO / RFO
|  |  | (P) 800-288-9488 / (F) 256-259-7478 |  |  | Next Gen Minicon
|  |  | http://russell.htpgusa.com |  |  | Air Cooled Condensing Unit
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
| REFRIGERANT | VOLTS / PHASE / HERTZ
|  | 208/230/1/60 |  | 208/230/3/60 | 460/3/60
| R404A | R*O130E4S-DA |  | R*O130E4S-EA | R*O130E4S-GA
|  | R*O150E4S-DA |  | R*O150E4S-EA | R*O150E4S-GA
|  | R*O180E4S-DA |  | R*O180E4S-EA | R*O180E4S-GA
|  | R*O200E4S-DA |  | R*O200E4S-EA | R*O200E4S-GA
|  | R*O250E4S-DA |  | R*O250E4S-EA | R*O250E4S-GA
|  | R*O300E4S-DA |  | R*O300E4S-EA | R*O300E4S-GA
|  | R*O350E4S-DA |  | R*O350E4S-EA | R*O350E4S-GA
|  | R*O400E4S-DA |  | R*O400E4S-EA | R*O400E4S-GA
|  | R*O450E4S-DA |  | R*O450E4S-EA | R*O450E4S-GA
|  | R*O500E4S-DA |  | R*O500E4S-EA | R*O500E4S-GA
|  | N/A |  | R*O600E4S-EA | R*O600E4S-GA
| R407A | R*O130E4S-DA |  | R*O130E4S-EA | R*O130E4S-GA
|  | R*O150E4S-DA |  | R*O150E4S-EA | R*O150E4S-GA
|  | R*O180E4S-DA |  | R*O180E4S-EA | R*O180E4S-GA
|  | R*O200E4S-DA |  | R*O200E4S-EA | R*O200E4S-GA
|  | R*O250E4S-DA |  | R*O250E4S-EA | R*O250E4S-GA
|  | R*O300E4S-DA |  | R*O300E4S-EA | R*O300E4S-GA
|  | R*O350E4S-DA |  | R*O350E4S-EA | R*O350E4S-GA
|  | R*O400E4S-DA |  | R*O400E4S-EA | R*O400E4S-GA
|  | R*O450E4S-DA |  | R*O450E4S-EA | R*O450E4S-GA |  |  | 3720
|  | R*O500E4S-DA |  | R*O500E4S-EA | R*O500E4S-GA
|  | N/A |  | R*O600E4S-EA | R*O600E4S-GA
| R407C | R*O130E4S-DA |  | R*O130E4S-EA | R*O130E4S-GA
|  | R*O150E4S-DA |  | R*O150E4S-EA | R*O150E4S-GA
|  | R*O180E4S-DA |  | R*O180E4S-EA | R*O180E4S-GA
|  | R*O200E4S-DA |  | R*O200E4S-EA | R*O200E4S-GA
|  | R*O250E4S-DA |  | R*O250E4S-EA | R*O250E4S-GA
|  | R*O300E4S-DA |  | R*O300E4S-EA | R*O300E4S-GA
|  | R*O350E4S-DA |  | R*O350E4S-EA | R*O350E4S-GA
|  | R*O400E4S-DA |  | R*O400E4S-EA | R*O400E4S-GA
|  | R*O450E4S-DA |  | R*O450E4S-EA | R*O450E4S-GA
|  | R*O500E4S-DA |  | R*O500E4S-EA | R*O500E4S-GA
|  | N/A |  | R*O600E4S-EA | R*O600E4S-GA
| R448A/R449A | R*O130E4S-DA |  | R*O130E4S-EA | R*O130E4S-GA
|  | R*O150E4S-DA |  | R*O150E4S-EA | R*O150E4S-GA
|  | R*O180E4S-DA |  | R*O180E4S-EA | R*O180E4S-GA
|  | R*O200E4S-DA |  | R*O200E4S-EA | R*O200E4S-GA
|  | R*O250E4S-DA |  | R*O250E4S-EA | R*O250E4S-GA
|  | R*O300E4S-DA |  | R*O300E4S-EA | R*O300E4S-GA
|  | R*O350E4S-DA |  | R*O350E4S-EA | R*O350E4S-GA
|  | R*O400E4S-DA |  | R*O400E4S-EA | R*O400E4S-GA
|  | R*O450E4S-DA |  | R*O450E4S-EA | R*O450E4S-GA
|  | R*O500E4S-DA |  | R*O500E4S-EA | R*O500E4S-GA
|  | N/A |  | R*O600E4S-EA | R*O600E4S-GA
NOTE | * Designates model style; "B" is non-flooded model / "F" is flooded model ("flood" = low ambient head press control valve)
R_SUB_INDEX_1115-A

## R_O130E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 12200 | 11130 | 10110 | 8280 | 7460 | 6690 | 5980 | 5330 | 4210 | 3720 |  | 3720
| +95 Deg F |  | 11670 | 10640 | 9670 | 7920 | 7140 | 6400 | 5730 | 5110 | 4040 | 3570
| +100 Deg F |  | 11130 | 10150 | 9220 | 7550 | 6810 | 6110 | 5470 | 4880 | 3860 | 3420
| +105 Deg F |  | 10580 | 9640 | 8760 | 7180 | 6470 | 5810 | 5200 | 4640 | 3670 | 3260
| +110 Deg F |  | 10010 | 9120 | 8290 | 6790 | 6120 | 5500 | 4920 | 4390 | 3480 | 3090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 5.9 Lb's | 11 Lb's | 2.3 Lb's | 7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9 | 40.3 | 0.5 | 4 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11650 | 10590 | 9610 | 7870 | 7100 | 6380 | 5700 | 5070 | 3880 | 3300 |  | 3720
| +95 Deg F |  | 11230 | 10220 | 9270 | 7590 | 6840 | 6140 | 5490 | 4880
| +100 Deg F |  | 10820 | 9850 | 8930 | 7300 | 6580 | 5910 | 5280 | 4680
| +105 Deg F |  | 10410 | 9470 | 8590 | 7020 | 6320 | 5670 | 5070 | 4490
| +110 Deg F |  | 9990 | 9090 | 8250 | 6740 | 6060 | 5440
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.45 Lb's | 12.1 Lb's | 2.5 Lb's | 7.7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9 | 40.3 | 0.5 | 4 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11150 | 10120 | 9130 | 7260 | 6380 | 5520 | 4690 | 3890 | 2320 |  |  | 3720
| +95 Deg F |  | 10830 | 9850 | 8880 | 7050 | 6180 | 5330 | 4500 | 3700
| +100 Deg F |  | 10520 | 9570 | 8630 | 6830 | 5970 | 5130 | 4300 | 3490
| +105 Deg F |  | 10210 | 9290 | 8380 | 6610 | 5750 | 4910 | 4080
| +110 Deg F |  | 9890 | 9000 | 8120 | 6370 | 5510 | 4670
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.7 Lb's | 12.7 Lb's | 2.4 Lb's | 7.7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9 | 40.3 | 0.5 | 4 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11100 | 10030 | 9070 | 7410 | 6680 | 6000 | 5340 | 4710 | 3410 | 2700 |  | 3720
| +95 Deg F |  | 10700 | 9680 | 8750 | 7160 | 6470 | 5820 | 5210 | 4630
| +100 Deg F |  | 10290 | 9310 | 8400 | 6880 | 6230 | 5630 | 5070 | 4520
| +105 Deg F |  | 9860 | 8900 | 8040 | 6580 | 5970 | 5410 | 4890 | 4390
| +110 Deg F |  | 9390 | 8460 | 7640 | 6250 | 5670 | 5160
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.1 Lb's | 11.6 Lb's | 2.4 Lb's | 7.32 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 9 | 40.3 | 0.5 | 4 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 12200 | 11130 | 10110 | 8280 | 7460 | 6690 | 5980 | 5330 | 4210 | 3720 |  | 3720
| +95 Deg F |  | 11670 | 10640 | 9670 | 7920 | 7140 | 6400 | 5730 | 5110 | 4040 | 3570
| +100 Deg F |  | 11130 | 10150 | 9220 | 7550 | 6810 | 6110 | 5470 | 4880 | 3860 | 3420
| +105 Deg F |  | 10580 | 9640 | 8760 | 7180 | 6470 | 5810 | 5200 | 4640 | 3670 | 3260
| +110 Deg F |  | 10010 | 9120 | 8290 | 6790 | 6120 | 5500 | 4920 | 4390 | 3480 | 3090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 5.9 Lb's | 11 Lb's | 2.3 Lb's | 7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 7.2 | 55.4 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11650 | 10590 | 9610 | 7870 | 7100 | 6380 | 5700 | 5070 | 3880 | 3300 |  | 3720
| +95 Deg F |  | 11230 | 10220 | 9270 | 7590 | 6840 | 6140 | 5490 | 4880
| +100 Deg F |  | 10820 | 9850 | 8930 | 7300 | 6580 | 5910 | 5280 | 4680
| +105 Deg F |  | 10410 | 9470 | 8590 | 7020 | 6320 | 5670 | 5070 | 4490
| +110 Deg F |  | 9990 | 9090 | 8250 | 6740 | 6060 | 5440
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.4 Lb's | 12.1 Lb's | 2.5 Lb's | 7.7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 7.2 | 55.4 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11150 | 10120 | 9130 | 7260 | 6380 | 5520 | 4690 | 3890 | 2320 |  |  | 3720
| +95 Deg F |  | 10830 | 9850 | 8880 | 7050 | 6180 | 5330 | 4500 | 3700
| +100 Deg F |  | 10520 | 9570 | 8630 | 6830 | 5970 | 5130 | 4300 | 3490
| +105 Deg F |  | 10210 | 9290 | 8380 | 6610 | 5750 | 4910 | 4080
| +110 Deg F |  | 9890 | 9000 | 8120 | 6370 | 5510 | 4670
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.7 Lb's | 12.7 Lb's | 2.4 Lb's | 7.7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 7.2 | 55.4 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11100 | 10030 | 9070 | 7410 | 6680 | 6000 | 5340 | 4710 | 3410 | 2700 |  | 3720
| +95 Deg F |  | 10700 | 9680 | 8750 | 7160 | 6470 | 5820 | 5210 | 4630
| +100 Deg F |  | 10290 | 9310 | 8400 | 6880 | 6230 | 5630 | 5070 | 4520
| +105 Deg F |  | 9860 | 8900 | 8040 | 6580 | 5970 | 5410 | 4890 | 4390
| +110 Deg F |  | 9390 | 8460 | 7640 | 6250 | 5670 | 5160
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.1 Lb's | 11.6 Lb's | 2.4 Lb's | 7.32 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 7.2 | 55.4 | 0.5 | 4 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 12200 | 11130 | 10110 | 8280 | 7460 | 6690 | 5980 | 5330 | 4210 | 3720 |  | 3720
| +95 Deg F |  | 11670 | 10640 | 9670 | 7920 | 7140 | 6400 | 5730 | 5110 | 4040 | 3570
| +100 Deg F |  | 11130 | 10150 | 9220 | 7550 | 6810 | 6110 | 5470 | 4880 | 3860 | 3420
| +105 Deg F |  | 10580 | 9640 | 8760 | 7180 | 6470 | 5810 | 5200 | 4640 | 3670 | 3260
| +110 Deg F |  | 10010 | 9120 | 8290 | 6790 | 6120 | 5500 | 4920 | 4390 | 3480 | 3090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 5.9 Lb's | 11 Lb's | 2.3 Lb's | 7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.4 | 28 | 0.4 | 2 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11650 | 10590 | 9610 | 7870 | 7100 | 6380 | 5700 | 5070 | 3880 | 3300 |  | 3720
| +95 Deg F |  | 11230 | 10220 | 9270 | 7590 | 6840 | 6140 | 5490 | 4880
| +100 Deg F |  | 10820 | 9850 | 8930 | 7300 | 6580 | 5910 | 5280 | 4680
| +105 Deg F |  | 10410 | 9470 | 8590 | 7020 | 6320 | 5670 | 5070 | 4490
| +110 Deg F |  | 9990 | 9090 | 8250 | 6740 | 6060 | 5440
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.4 Lb's | 12.1 Lb's | 2.5 Lb's | 7.7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.4 | 28 | 0.4 | 2 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11150 | 10120 | 9130 | 7260 | 6380 | 5520 | 4690 | 3890 | 2320 |  |  | 3720
| +95 Deg F |  | 10830 | 9850 | 8880 | 7050 | 6180 | 5330 | 4500 | 3700
| +100 Deg F |  | 10520 | 9570 | 8630 | 6830 | 5970 | 5130 | 4300 | 3490
| +105 Deg F |  | 10210 | 9290 | 8380 | 6610 | 5750 | 4910 | 4080
| +110 Deg F |  | 9890 | 9000 | 8120 | 6370 | 5510 | 4670
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.7 Lb's | 12.7 Lb's | 2.4 Lb's | 7.7 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.4 | 28 | 0.4 | 2 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O130E4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 11100 | 10030 | 9070 | 7410 | 6680 | 6000 | 5340 | 4710 | 3410 | 2700 |  | 3720
| +95 Deg F |  | 10700 | 9680 | 8750 | 7160 | 6470 | 5820 | 5210 | 4630
| +100 Deg F |  | 10290 | 9310 | 8400 | 6880 | 6230 | 5630 | 5070 | 4520
| +105 Deg F |  | 9860 | 8900 | 8040 | 6580 | 5970 | 5410 | 4890 | 4390
| +110 Deg F |  | 9390 | 8460 | 7640 | 6250 | 5670 | 5160
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS09KAE |  | 1.33 | 1 | 6.1 Lb's | 11.6 Lb's | 2.4 Lb's | 7.32 Lb's | 3/8" | 5/8" | 70 | 176 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.4 | 28 | 0.4 | 2 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15740 | 14270 | 12910 | 10480 | 9400 | 8410 | 7500 | 6670 | 5230 | 4620 |  | 3720
| +95 Deg F |  | 15090 | 13690 | 12380 | 10050 | 9010 | 8060 | 7190 | 6400 | 5030 | 4440
| +100 Deg F |  | 14430 | 13080 | 11830 | 9600 | 8610 | 7710 | 6880 | 6120 | 4810 | 4260
| +105 Deg F |  | 13750 | 12470 | 11270 | 9140 | 8200 | 7340 | 6550 | 5830 | 4600 | 4070
| +110 Deg F |  | 13060 | 11840 | 10700 | 8670 | 7780 | 6960 | 6220 | 5540 | 4370 | 3870
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 4.3 Lb's | 6.1 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 11.3 | 55 | 1 | 6 | 20 | 16.1 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 14570 | 13210 | 11960 | 9740 | 8760 | 7850 | 7000 | 6210 | 4730 | 4020 |  | 3720
| +95 Deg F |  | 14070 | 12750 | 11540 | 9390 | 8440 | 7560 | 6740 | 5970
| +100 Deg F |  | 13560 | 12290 | 11120 | 9040 | 8120 | 7270 | 6480 | 5740
| +105 Deg F |  | 13060 | 11830 | 10690 | 8690 | 7810 | 6990 | 6220 | 5510
| +110 Deg F |  | 12540 | 11360 | 10270 | 8340 | 7490 | 6700
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 12.1 Lb's | 15 Lb's | 4.1 Lb's | 6.72 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 11.3 | 55 | 1 | 6 | 20 | 16.1 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 13950 | 12630 | 11360 | 8980 | 7870 | 6790 | 5760 | 4760 | 2830 |  |  | 3720
| +95 Deg F |  | 13560 | 12280 | 11060 | 8730 | 7620 | 6560 | 5530 | 4530
| +100 Deg F |  | 13180 | 11940 | 10750 | 8460 | 7370 | 6310 | 5280 | 4280
| +105 Deg F |  | 12810 | 11600 | 10430 | 8180 | 7100 | 6050 | 5010
| +110 Deg F |  | 12410 | 11250 | 10110 | 7890 | 6810 | 5760
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 12.7 Lb's | 15.7 Lb's | 4.1 Lb's | 6.7 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 11.3 | 55 | 1 | 6 | 20 | 16.1 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-DA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 13960 | 12580 | 11350 | 9220 | 8290 | 7420 | 6600 | 5800 | 4180 | 3310 |  | 3720
| +95 Deg F |  | 13480 | 12140 | 10950 | 8910 | 8020 | 7210 | 6440 | 5690
| +100 Deg F |  | 12970 | 11680 | 10530 | 8570 | 7730 | 6970 | 6250 | 5570
| +105 Deg F |  | 12440 | 11180 | 10060 | 8200 | 7420 | 6700 | 6040 | 5420
| +110 Deg F |  | 11850 | 10630 | 9560 | 7780 | 7050 | 6390
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 11.6 Lb's | 14.3 Lb's | 3.9 Lb's | 6.41 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 11.3 | 55 | 1 | 6 | 20 | 16.1 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15740 | 14270 | 12910 | 10480 | 9400 | 8410 | 7500 | 6670 | 5230 | 4620 |  | 3720
| +95 Deg F |  | 15090 | 13690 | 12380 | 10050 | 9010 | 8060 | 7190 | 6400 | 5030 | 4440
| +100 Deg F |  | 14430 | 13080 | 11830 | 9600 | 8610 | 7710 | 6880 | 6120 | 4810 | 4260
| +105 Deg F |  | 13750 | 12470 | 11270 | 9140 | 8200 | 7340 | 6550 | 5830 | 4600 | 4070
| +110 Deg F |  | 13060 | 11840 | 10700 | 8670 | 7780 | 6960 | 6220 | 5540 | 4370 | 3870
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 4.3 Lb's | 6.1 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.3 | 58 | 1 | 6 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 14570 | 13210 | 11960 | 9740 | 8760 | 7850 | 7000 | 6210 | 4730 | 4020 |  | 3720
| +95 Deg F |  | 14070 | 12750 | 11540 | 9390 | 8440 | 7560 | 6740 | 5970
| +100 Deg F |  | 13560 | 12290 | 11120 | 9040 | 8120 | 7270 | 6480 | 5740
| +105 Deg F |  | 13060 | 11830 | 10690 | 8690 | 7810 | 6990 | 6220 | 5510
| +110 Deg F |  | 12540 | 11360 | 10270 | 8340 | 7490 | 6700
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 12.1 Lb's | 15 Lb's | 4.1 Lb's | 6.72 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.3 | 58 | 1 | 6 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 13950 | 12630 | 11360 | 8980 | 7870 | 6790 | 5760 | 4760 | 2830 |  |  | 3720
| +95 Deg F |  | 13560 | 12280 | 11060 | 8730 | 7620 | 6560 | 5530 | 4530
| +100 Deg F |  | 13180 | 11940 | 10750 | 8460 | 7370 | 6310 | 5280 | 4280
| +105 Deg F |  | 12810 | 11600 | 10430 | 8180 | 7100 | 6050 | 5010
| +110 Deg F |  | 12410 | 11250 | 10110 | 7890 | 6810 | 5760
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 12.7 Lb's | 15.7 Lb's | 4.1 Lb's | 6.7 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.3 | 58 | 1 | 6 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-EA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 13960 | 12580 | 11350 | 9220 | 8290 | 7420 | 6600 | 5800 | 4180 | 3310 |  | 3720
| +95 Deg F |  | 13480 | 12140 | 10950 | 8910 | 8020 | 7210 | 6440 | 5690
| +100 Deg F |  | 12970 | 11680 | 10530 | 8570 | 7730 | 6970 | 6250 | 5570
| +105 Deg F |  | 12440 | 11180 | 10060 | 8200 | 7420 | 6700 | 6040 | 5420
| +110 Deg F |  | 11850 | 10630 | 9560 | 7780 | 7050 | 6390
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 11.6 Lb's | 14.3 Lb's | 3.9 Lb's | 6.41 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.3 | 58 | 1 | 6 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15740 | 14270 | 12910 | 10480 | 9400 | 8410 | 7500 | 6670 | 5230 | 4620 |  | 3720
| +95 Deg F |  | 15090 | 13690 | 12380 | 10050 | 9010 | 8060 | 7190 | 6400 | 5030 | 4440
| +100 Deg F |  | 14430 | 13080 | 11830 | 9600 | 8610 | 7710 | 6880 | 6120 | 4810 | 4260
| +105 Deg F |  | 13750 | 12470 | 11270 | 9140 | 8200 | 7340 | 6550 | 5830 | 4600 | 4070
| +110 Deg F |  | 13060 | 11840 | 10700 | 8670 | 7780 | 6960 | 6220 | 5540 | 4370 | 3870
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 11 Lb's | 13.6 Lb's | 4.3 Lb's | 6.1 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.8 | 28 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 14570 | 13210 | 11960 | 9740 | 8760 | 7850 | 7000 | 6210 | 4730 | 4020 |  | 3720
| +95 Deg F |  | 14070 | 12750 | 11540 | 9390 | 8440 | 7560 | 6740 | 5970
| +100 Deg F |  | 13560 | 12290 | 11120 | 9040 | 8120 | 7270 | 6480 | 5740
| +105 Deg F |  | 13060 | 11830 | 10690 | 8690 | 7810 | 6990 | 6220 | 5510
| +110 Deg F |  | 12540 | 11360 | 10270 | 8340 | 7490 | 6700
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 12.1 Lb's | 15 Lb's | 4.1 Lb's | 6.72 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.8 | 28 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 13950 | 12630 | 11360 | 8980 | 7870 | 6790 | 5760 | 4760 | 2830 |  |  | 3720
| +95 Deg F |  | 13560 | 12280 | 11060 | 8730 | 7620 | 6560 | 5530 | 4530
| +100 Deg F |  | 13180 | 11940 | 10750 | 8460 | 7370 | 6310 | 5280 | 4280
| +105 Deg F |  | 12810 | 11600 | 10430 | 8180 | 7100 | 6050 | 5010
| +110 Deg F |  | 12410 | 11250 | 10110 | 7890 | 6810 | 5760
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 12.7 Lb's | 15.7 Lb's | 4.1 Lb's | 6.7 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.8 | 28 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O150E4S-GA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 13960 | 12580 | 11350 | 9220 | 8290 | 7420 | 6600 | 5800 | 4180 | 3310 |  | 3720
| +95 Deg F |  | 13480 | 12140 | 10950 | 8910 | 8020 | 7210 | 6440 | 5690
| +100 Deg F |  | 12970 | 11680 | 10530 | 8570 | 7730 | 6970 | 6250 | 5570
| +105 Deg F |  | 12440 | 11180 | 10060 | 8200 | 7420 | 6700 | 6040 | 5420
| +110 Deg F |  | 11850 | 10630 | 9560 | 7780 | 7050 | 6390
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS11KAE |  | 1.5 | 2 | 11.6 Lb's | 14.3 Lb's | 3.9 Lb's | 6.41 Lb's | 1/2" | 7/8" | 71 | 185 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 3.8 | 28 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 17610 | 15990 | 14490 | 11790 | 10600 | 9500 | 8490 | 7560 | 5950 | 5250 |  | 3720
| +95 Deg F |  | 16870 | 15320 | 13880 | 11290 | 10150 | 9100 | 8130 | 7250 | 5710 | 5050
| +100 Deg F |  | 16110 | 14640 | 13260 | 10780 | 9690 | 8690 | 7770 | 6930 | 5470 | 4840
| +105 Deg F |  | 15350 | 13940 | 12620 | 10260 | 9220 | 8270 | 7400 | 6600 | 5210 | 4620
| +110 Deg F |  | 14550 | 13220 | 11970 | 9730 | 8740 | 7840 | 7010 | 6260 | 4950 | 4390
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 12.7 Lb's | 15.7 Lb's | 4.3 Lb's | 6.1 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 10.8 | 56 | 1 | 6 | 20 | 15.5 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 16420 | 14900 | 13510 | 11040 | 9940 | 8920 | 7960 | 7070 | 5390 | 4580 |  | 3720
| +95 Deg F |  | 15850 | 14390 | 13040 | 10650 | 9580 | 8590 | 7670 | 6800
| +100 Deg F |  | 15280 | 13860 | 12560 | 10250 | 9220 | 8270 | 7370 | 6530
| +105 Deg F |  | 14700 | 13340 | 12080 | 9860 | 8860 | 7940 | 7080 | 6270
| +110 Deg F |  | 14120 | 12810 | 11600 | 9460 | 8510 | 7620
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 12.1 Lb's | 15 Lb's | 4.1 Lb's | 6.72 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 10.8 | 56 | 1 | 6 | 20 | 15.5 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15720 | 14240 | 12840 | 10180 | 8930 | 7720 | 6550 | 5420 | 3230 |  |  | 3720
| +95 Deg F |  | 15280 | 13860 | 12490 | 9900 | 8650 | 7450 | 6290 | 5150
| +100 Deg F |  | 14850 | 13470 | 12140 | 9590 | 8370 | 7180 | 6010 | 4860
| +105 Deg F |  | 14410 | 13080 | 11780 | 9280 | 8060 | 6870 | 5700
| +110 Deg F |  | 17840 | 16130 | 14480 | 11330 | 9830 | 8370 | 6940
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 12.7 Lb's | 15.7 Lb's | 4.1 Lb's | 6.7 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 10.8 | 56 | 1 | 6 | 20 | 15.5 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-DA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15710 | 14180 | 12810 | 10440 | 9400 | 8430 | 7490 | 6600 | 4760 | 3770 |  | 3720
| +95 Deg F |  | 15170 | 13690 | 12360 | 10090 | 9100 | 8180 | 7320 | 6480
| +100 Deg F |  | 14600 | 13150 | 11870 | 9700 | 8770 | 7920 | 7110 | 6330
| +105 Deg F |  | 13990 | 12590 | 11350 | 9290 | 8400 | 7610 | 6860 | 6160
| +110 Deg F |  | 13330 | 11980 | 10790 | 8820 | 8000 | 7250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 11.6 Lb's | 14.3 Lb's | 3.9 Lb's | 6.41 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 10.8 | 56 | 1 | 6 | 20 | 15.5 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 17610 | 15990 | 14490 | 11790 | 10600 | 9500 | 8490 | 7560 | 5950 | 5250 |  | 3720
| +95 Deg F |  | 16870 | 15320 | 13880 | 11290 | 10150 | 9100 | 8130 | 7250 | 5710 | 5050
| +100 Deg F |  | 16110 | 14640 | 13260 | 10780 | 9690 | 8690 | 7770 | 6930 | 5470 | 4840
| +105 Deg F |  | 15350 | 13940 | 12620 | 10260 | 9220 | 8270 | 7400 | 6600 | 5210 | 4620
| +110 Deg F |  | 14550 | 13220 | 11970 | 9730 | 8740 | 7840 | 7010 | 6260 | 4950 | 4390
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 12.7 Lb's | 15.7 Lb's | 4.3 Lb's | 6.1 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 58 | 1 | 6 | 15 | 15 | 20 | 19.7 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 16420 | 14900 | 13510 | 11040 | 9940 | 8920 | 7960 | 7070 | 5390 | 4580 |  | 3720
| +95 Deg F |  | 15850 | 14390 | 13040 | 10650 | 9580 | 8590 | 7670 | 6800
| +100 Deg F |  | 15280 | 13860 | 12560 | 10250 | 9220 | 8270 | 7370 | 6530
| +105 Deg F |  | 14700 | 13340 | 12080 | 9860 | 8860 | 7940 | 7080 | 6270
| +110 Deg F |  | 14120 | 12810 | 11600 | 9460 | 8510 | 7620
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 12.1 Lb's | 15 Lb's | 4.1 Lb's | 6.72 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 58 | 1 | 6 | 15 | 15 | 20 | 19.8 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15720 | 14240 | 12840 | 10180 | 8930 | 7720 | 6550 | 5420 | 3230 |  |  | 3720
| +95 Deg F |  | 15280 | 13860 | 12490 | 9900 | 8650 | 7450 | 6290 | 5150
| +100 Deg F |  | 14850 | 13470 | 12140 | 9590 | 8370 | 7180 | 6010 | 4860
| +105 Deg F |  | 14410 | 13080 | 11780 | 9280 | 8060 | 6870 | 5700
| +110 Deg F |  | 17840 | 16130 | 14480 | 11330 | 9830 | 8370 | 6940
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 12.7 Lb's | 15.7 Lb's | 4.1 Lb's | 6.7 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 58 | 1 | 6 | 15 | 15 | 20 | 19.8 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-EA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15710 | 14180 | 12810 | 10440 | 9400 | 8430 | 7490 | 6600 | 4760 | 3770 |  | 3720
| +95 Deg F |  | 15170 | 13690 | 12360 | 10090 | 9100 | 8180 | 7320 | 6480
| +100 Deg F |  | 14600 | 13150 | 11870 | 9700 | 8770 | 7920 | 7110 | 6330
| +105 Deg F |  | 13990 | 12590 | 11350 | 9290 | 8400 | 7610 | 6860 | 6160
| +110 Deg F |  | 13330 | 11980 | 10790 | 8820 | 8000 | 7250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 11.6 Lb's | 14.3 Lb's | 3.9 Lb's | 6.41 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 8.7 | 58 | 1 | 6 | 15 | 15 | 20 | 19.8 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 17610 | 15990 | 14490 | 11790 | 10600 | 9500 | 8490 | 7560 | 5950 | 5250 |  | 3720
| +95 Deg F |  | 16870 | 15320 | 13880 | 11290 | 10150 | 9100 | 8130 | 7250 | 5710 | 5050
| +100 Deg F |  | 16110 | 14640 | 13260 | 10780 | 9690 | 8690 | 7770 | 6930 | 5470 | 4840
| +105 Deg F |  | 15350 | 13940 | 12620 | 10260 | 9220 | 8270 | 7400 | 6600 | 5210 | 4620
| +110 Deg F |  | 14550 | 13220 | 11970 | 9730 | 8740 | 7840 | 7010 | 6260 | 4950 | 4390
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 11 Lb's | 13.6 Lb's | 4.3 Lb's | 6.1 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.3 | 29 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 16420 | 14900 | 13510 | 11040 | 9940 | 8920 | 7960 | 7070 | 5390 | 4580 |  | 3720
| +95 Deg F |  | 15850 | 14390 | 13040 | 10650 | 9580 | 8590 | 7670 | 6800
| +100 Deg F |  | 15280 | 13860 | 12560 | 10250 | 9220 | 8270 | 7370 | 6530
| +105 Deg F |  | 14700 | 13340 | 12080 | 9860 | 8860 | 7940 | 7080 | 6270
| +110 Deg F |  | 14120 | 12810 | 11600 | 9460 | 8510 | 7620
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 12.1 Lb's | 15 Lb's | 4.1 Lb's | 6.72 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.3 | 29 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15720 | 14240 | 12840 | 10180 | 8930 | 7720 | 6550 | 5420 | 3230 |  |  | 3720
| +95 Deg F |  | 15280 | 13860 | 12490 | 9900 | 8650 | 7450 | 6290 | 5150
| +100 Deg F |  | 14850 | 13470 | 12140 | 9590 | 8370 | 7180 | 6010 | 4860
| +105 Deg F |  | 14410 | 13080 | 11780 | 9280 | 8060 | 6870 | 5700
| +110 Deg F |  | 17840 | 16130 | 14480 | 11330 | 9830 | 8370 | 6940
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 12.7 Lb's | 15.7 Lb's | 4.1 Lb's | 6.7 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.3 | 29 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O180E4S-GA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 15710 | 14180 | 12810 | 10440 | 9400 | 8430 | 7490 | 6600 | 4760 | 3770 |  | 3720
| +95 Deg F |  | 15170 | 13690 | 12360 | 10090 | 9100 | 8180 | 7320 | 6480
| +100 Deg F |  | 14600 | 13150 | 11870 | 9700 | 8770 | 7920 | 7110 | 6330
| +105 Deg F |  | 13990 | 12590 | 11350 | 9290 | 8400 | 7610 | 6860 | 6160
| +110 Deg F |  | 13330 | 11980 | 10790 | 8820 | 8000 | 7250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZF13KAE |  | 1.75 | 2 | 11.6 Lb's | 14.3 Lb's | 3.9 Lb's | 6.41 Lb's | 1/2" | 7/8" | 71 | 189 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.3 | 29 | 0.8 | 3 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 22160 | 20050 | 18100 | 14600 | 13060 | 11660 | 10390 | 9230 | 7240 | 6380 |  | 3720
| +95 Deg F |  | 21260 | 19230 | 17350 | 14010 | 12530 | 11190 | 9970 | 8860 | 6950 | 6140
| +100 Deg F |  | 20330 | 18400 | 16600 | 13400 | 11990 | 10700 | 9540 | 8480 | 6660 | 5890
| +105 Deg F |  | 19400 | 17540 | 15830 | 12780 | 11440 | 10210 | 9090 | 8090 | 6360 | 5630
| +110 Deg F |  | 18440 | 16680 | 15040 | 12140 | 10860 | 9700 | 8640 | 7680 | 6050 | 5350
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 13.6 Lb's | 20.9 Lb's | 5.3 Lb's | 7.83 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.1 | 68 | 1 | 10 | 25 | 19.6 | 30 | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 20240 | 18320 | 16560 | 13470 | 12110 | 10850 | 9680 | 8580 | 6540 | 5560 |  | 3720
| +95 Deg F |  | 19560 | 17700 | 15990 | 13000 | 11680 | 10460 | 9330 | 8260
| +100 Deg F |  | 18880 | 17080 | 15420 | 12520 | 11240 | 10070 | 8970 | 7940
| +105 Deg F |  | 18190 | 16450 | 14850 | 12040 | 10810 | 9670 | 8610 | 7620
| +110 Deg F |  | 17490 | 15810 | 14270 | 11570 | 10380 | 9280
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 15 Lb's | 23.1 Lb's | 5.83 Lb's | 8.63 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.1 | 68 | 1 | 10 | 29.6 | 19.6 | 30 | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 19380 | 17510 | 15740 | 12420 | 10880 | 9390 | 7960 | 6580 | 3910 |  |  | 3720
| +95 Deg F |  | 18860 | 17050 | 15320 | 12080 | 10550 | 9080 | 7650 | 6260
| +100 Deg F |  | 18350 | 16600 | 14900 | 11710 | 10200 | 8740 | 7310 | 5910
| +105 Deg F |  | 17840 | 16130 | 14480 | 11330 | 9830 | 8370 | 6940
| +110 Deg F |  | 17320 | 15660 | 14040 | 10940 | 9440 | 7970
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 15.7 Lb's | 24.1 Lb's | 5.8 Lb's | 8.6 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.1 | 68 | 1 | 10 | 29.6 | 19.6 | 30 | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 19370 | 17440 | 15700 | 12740 | 11450 | 10250 | 9120 | 8010 | 5780 | 4580 |  | 3720
| +95 Deg F |  | 18730 | 16840 | 15160 | 12320 | 11090 | 9960 | 8910 | 7870
| +100 Deg F |  | 18050 | 16220 | 14580 | 11860 | 10690 | 9640 | 8650 | 7700
| +105 Deg F |  | 17320 | 15540 | 13960 | 11350 | 10260 | 9270 | 8350 | 7490
| +110 Deg F |  | 16510 | 14790 | 13270 | 10790 | 9760 | 8840
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 14.3 Lb's | 22.1 Lb's | 5.6 Lb's | 8.23 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 14.1 | 68 | 1 | 10 | 29.6 | 19.6 | 30 | 32.2 | 40
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 22160 | 20050 | 18100 | 14600 | 13060 | 11660 | 10390 | 9230 | 7240 | 6380 |  | 3720
| +95 Deg F |  | 21260 | 19230 | 17350 | 14010 | 12530 | 11190 | 9970 | 8860 | 6950 | 6140
| +100 Deg F |  | 20330 | 18400 | 16600 | 13400 | 11990 | 10700 | 9540 | 8480 | 6660 | 5890
| +105 Deg F |  | 19400 | 17540 | 15830 | 12780 | 11440 | 10210 | 9090 | 8090 | 6360 | 5630
| +110 Deg F |  | 18440 | 16680 | 15040 | 12140 | 10860 | 9700 | 8640 | 7680 | 6050 | 5350
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 13.6 Lb's | 20.9 Lb's | 5.3 Lb's | 7.83 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.6 | 58 | 1 | 10 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 20240 | 18320 | 16560 | 13470 | 12110 | 10850 | 9680 | 8580 | 6540 | 5560 |  | 3720
| +95 Deg F |  | 19560 | 17700 | 15990 | 13000 | 11680 | 10460 | 9330 | 8260
| +100 Deg F |  | 18880 | 17080 | 15420 | 12520 | 11240 | 10070 | 8970 | 7940
| +105 Deg F |  | 18190 | 16450 | 14850 | 12040 | 10810 | 9670 | 8610 | 7620
| +110 Deg F |  | 17490 | 15810 | 14270 | 11570 | 10380 | 9280
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 15 Lb's | 23.1 Lb's | 5.83 Lb's | 8.63 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.6 | 58 | 1 | 10 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 19380 | 17510 | 15740 | 12420 | 10880 | 9390 | 7960 | 6580 | 3910 |  |  | 3720
| +95 Deg F |  | 18860 | 17050 | 15320 | 12080 | 10550 | 9080 | 7650 | 6260
| +100 Deg F |  | 18350 | 16600 | 14900 | 11710 | 10200 | 8740 | 7310 | 5910
| +105 Deg F |  | 17840 | 16130 | 14480 | 11330 | 9830 | 8370 | 6940
| +110 Deg F |  | 17320 | 15660 | 14040 | 10940 | 9440 | 7970
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 15.7 Lb's | 24.1 Lb's | 5.8 Lb's | 8.6 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.6 | 58 | 1 | 10 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 19370 | 17440 | 15700 | 12740 | 11450 | 10250 | 9120 | 8010 | 5780 | 4580 |  | 3720
| +95 Deg F |  | 18730 | 16840 | 15160 | 12320 | 11090 | 9960 | 8910 | 7870
| +100 Deg F |  | 18050 | 16220 | 14580 | 11860 | 10690 | 9640 | 8650 | 7700
| +105 Deg F |  | 17320 | 15540 | 13960 | 11350 | 10260 | 9270 | 8350 | 7490
| +110 Deg F |  | 16510 | 14790 | 13270 | 10790 | 9760 | 8840
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 14.3 Lb's | 22.1 Lb's | 5.6 Lb's | 8.23 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 9.6 | 58 | 1 | 10 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 22160 | 20050 | 18100 | 14600 | 13060 | 11660 | 10390 | 9230 | 7240 | 6380 |  | 3720
| +95 Deg F |  | 21260 | 19230 | 17350 | 14010 | 12530 | 11190 | 9970 | 8860 | 6950 | 6140
| +100 Deg F |  | 20330 | 18400 | 16600 | 13400 | 11990 | 10700 | 9540 | 8480 | 6660 | 5890
| +105 Deg F |  | 19400 | 17540 | 15830 | 12780 | 11440 | 10210 | 9090 | 8090 | 6360 | 5630
| +110 Deg F |  | 18440 | 16680 | 15040 | 12140 | 10860 | 9700 | 8640 | 7680 | 6050 | 5350
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 13.6 Lb's | 20.9 Lb's | 5.3 Lb's | 7.83 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.8 | 29 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 20240 | 18320 | 16560 | 13470 | 12110 | 10850 | 9680 | 8580 | 6540 | 5560 |  | 3720
| +95 Deg F |  | 19560 | 17700 | 15990 | 13000 | 11680 | 10460 | 9330 | 8260
| +100 Deg F |  | 18880 | 17080 | 15420 | 12520 | 11240 | 10070 | 8970 | 7940
| +105 Deg F |  | 18190 | 16450 | 14850 | 12040 | 10810 | 9670 | 8610 | 7620
| +110 Deg F |  | 17490 | 15810 | 14270 | 11570 | 10380 | 9280
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 15 Lb's | 23.1 Lb's | 5.83 Lb's | 8.63 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.8 | 29 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 19380 | 17510 | 15740 | 12420 | 10880 | 9390 | 7960 | 6580 | 3910 |  |  | 3720
| +95 Deg F |  | 18860 | 17050 | 15320 | 12080 | 10550 | 9080 | 7650 | 6260
| +100 Deg F |  | 18350 | 16600 | 14900 | 11710 | 10200 | 8740 | 7310 | 5910
| +105 Deg F |  | 17840 | 16130 | 14480 | 11330 | 9830 | 8370 | 6940
| +110 Deg F |  | 17320 | 15660 | 14040 | 10940 | 9440 | 7970
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 15.7 Lb's | 24.1 Lb's | 5.8 Lb's | 8.6 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.8 | 29 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O200E4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 19370 | 17440 | 15700 | 12740 | 11450 | 10250 | 9120 | 8010 | 5780 | 4580 |  | 3720
| +95 Deg F |  | 18730 | 16840 | 15160 | 12320 | 11090 | 9960 | 8910 | 7870
| +100 Deg F |  | 18050 | 16220 | 14580 | 11860 | 10690 | 9640 | 8650 | 7700
| +105 Deg F |  | 17320 | 15540 | 13960 | 11350 | 10260 | 9270 | 8350 | 7490
| +110 Deg F |  | 16510 | 14790 | 13270 | 10790 | 9760 | 8840
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS15KAE |  | 2 | 2 | 14.3 Lb's | 22.1 Lb's | 5.6 Lb's | 8.23 Lb's | 1/2" | 7/8" | 71 | 194 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 4.8 | 29 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 24190 | 21960 | 19880 | 16150 | 14470 | 12930 | 11530 | 10250 | 8050 | 7100 |  | 3720
| +95 Deg F |  | 23190 | 21060 | 19060 | 15480 | 13880 | 12400 | 11060 | 9830 | 7730 | 6830
| +100 Deg F |  | 22180 | 20130 | 18220 | 14790 | 13270 | 11860 | 10570 | 9410 | 7400 | 6550
| +105 Deg F |  | 21140 | 19190 | 17360 | 14090 | 12640 | 11300 | 10070 | 8960 | 7060 | 6260
| +110 Deg F |  | 20080 | 18220 | 16480 | 13380 | 12000 | 10720 | 9560 | 8510 | 6710 | 5950
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 5.3 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16.2 | 75 | 1 | 10 | 25 | 22.2 | 35 | 32.2 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 22610 | 20490 | 18540 | 15100 | 13580 | 12180 | 10870 | 9640 | 7350 | 6260 |  | 3720
| +95 Deg F |  | 21850 | 19800 | 17900 | 14570 | 13100 | 11740 | 10470 | 9280
| +100 Deg F |  | 21080 | 19100 | 17260 | 14040 | 12620 | 11300 | 10080 | 8920
| +105 Deg F |  | 20310 | 18390 | 16620 | 13510 | 12130 | 10860 | 9680 | 8570
| +110 Deg F |  | 19530 | 17690 | 15980 | 12980 | 11650 | 10430
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 15 Lb's | 23.1 Lb's | 5.83 Lb's | 8.63 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16.2 | 75 | 1 | 10 | 25 | 22.2 | 35 | 32.2 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 21650 | 19590 | 17620 | 13930 | 12200 | 10540 | 8940 | 7390 | 4400 |  |  | 3720
| +95 Deg F |  | 21060 | 19080 | 17150 | 13540 | 11830 | 10190 | 8590 | 7030
| +100 Deg F |  | 20490 | 18560 | 16680 | 13140 | 11450 | 9810 | 8210 | 6640
| +105 Deg F |  | 19910 | 18040 | 16210 | 12720 | 11030 | 9400 | 7800
| +110 Deg F |  | 19330 | 17520 | 15730 | 12270 | 10600 | 8960
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 15.7 Lb's | 24.1 Lb's | 5.8 Lb's | 8.6 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16.2 | 75 | 1 | 10 | 25 | 22.2 | 35 | 32.2 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 21560 | 19430 | 17510 | 14230 | 12790 | 11470 | 10200 | 8970 | 6470 | 5130 |  | 3720
| +95 Deg F |  | 20840 | 18770 | 16900 | 13750 | 12390 | 11140 | 9950 | 8810
| +100 Deg F |  | 20070 | 18060 | 16260 | 13240 | 11960 | 10780 | 9680 | 8620
| +105 Deg F |  | 19260 | 17300 | 15570 | 12680 | 11460 | 10370 | 9350 | 8390
| +110 Deg F |  | 18370 | 16480 | 14800 | 12050 | 10910 | 9890
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 14.3 Lb's | 22.1 Lb's | 5.6 Lb's | 8.23 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 16.2 | 75 | 1 | 10 | 25 | 22.2 | 35 | 32.2 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 24190 | 21960 | 19880 | 16150 | 14470 | 12930 | 11530 | 10250 | 8050 | 7100 |  | 3720
| +95 Deg F |  | 23190 | 21060 | 19060 | 15480 | 13880 | 12400 | 11060 | 9830 | 7730 | 6830
| +100 Deg F |  | 22180 | 20130 | 18220 | 14790 | 13270 | 11860 | 10570 | 9410 | 7400 | 6550
| +105 Deg F |  | 21140 | 19190 | 17360 | 14090 | 12640 | 11300 | 10070 | 8960 | 7060 | 6260
| +110 Deg F |  | 20080 | 18220 | 16480 | 13380 | 12000 | 10720 | 9560 | 8510 | 6710 | 5950
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 5.3 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 12.3 | 73 | 1 | 10 | 25 | 17.3 | 25 | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 22610 | 20490 | 18540 | 15100 | 13580 | 12180 | 10870 | 9640 | 7350 | 6260 |  | 3720
| +95 Deg F |  | 21850 | 19800 | 17900 | 14570 | 13100 | 11740 | 10470 | 9280
| +100 Deg F |  | 21080 | 19100 | 17260 | 14040 | 12620 | 11300 | 10080 | 8920
| +105 Deg F |  | 20310 | 18390 | 16620 | 13510 | 12130 | 10860 | 9680 | 8570
| +110 Deg F |  | 19530 | 17690 | 15980 | 12980 | 11650 | 10430
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 15 Lb's | 23.1 Lb's | 5.83 Lb's | 8.63 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 12.3 | 73 | 1 | 10 | 25 | 17.3 | 25 | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 21650 | 19590 | 17620 | 13930 | 12200 | 10540 | 8940 | 7390 | 4400 |  |  | 3720
| +95 Deg F |  | 21060 | 19080 | 17150 | 13540 | 11830 | 10190 | 8590 | 7030
| +100 Deg F |  | 20490 | 18560 | 16680 | 13140 | 11450 | 9810 | 8210 | 6640
| +105 Deg F |  | 19910 | 18040 | 16210 | 12720 | 11030 | 9400 | 7800
| +110 Deg F |  | 19330 | 17520 | 15730 | 12270 | 10600 | 8960
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 15.7 Lb's | 24.1 Lb's | 5.8 Lb's | 8.6 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 12.3 | 73 | 1 | 10 | 25 | 17.3 | 25 | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 21560 | 19430 | 17510 | 14230 | 12790 | 11470 | 10200 | 8970 | 6470 | 5130 |  | 3720
| +95 Deg F |  | 20840 | 18770 | 16900 | 13750 | 12390 | 11140 | 9950 | 8810
| +100 Deg F |  | 20070 | 18060 | 16260 | 13240 | 11960 | 10780 | 9680 | 8620
| +105 Deg F |  | 19260 | 17300 | 15570 | 12680 | 11460 | 10370 | 9350 | 8390
| +110 Deg F |  | 18370 | 16480 | 14800 | 12050 | 10910 | 9890
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 14.3 Lb's | 22.1 Lb's | 5.6 Lb's | 8.23 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 12.3 | 73 | 1 | 10 | 25 | 17.3 | 25 | 32.2 | 35
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 24190 | 21960 | 19880 | 16150 | 14470 | 12930 | 11530 | 10250 | 8050 | 7100 |  | 3720
| +95 Deg F |  | 23190 | 21060 | 19060 | 15480 | 13880 | 12400 | 11060 | 9830 | 7730 | 6830
| +100 Deg F |  | 22180 | 20130 | 18220 | 14790 | 13270 | 11860 | 10570 | 9410 | 7400 | 6550
| +105 Deg F |  | 21140 | 19190 | 17360 | 14090 | 12640 | 11300 | 10070 | 8960 | 7060 | 6260
| +110 Deg F |  | 20080 | 18220 | 16480 | 13380 | 12000 | 10720 | 9560 | 8510 | 6710 | 5950
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 13.6 Lb's | 20.9 Lb's | 5.3 Lb's | 7.83 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.8 | 38 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 22610 | 20490 | 18540 | 15100 | 13580 | 12180 | 10870 | 9640 | 7350 | 6260 |  | 3720
| +95 Deg F |  | 21850 | 19800 | 17900 | 14570 | 13100 | 11740 | 10470 | 9280
| +100 Deg F |  | 21080 | 19100 | 17260 | 14040 | 12620 | 11300 | 10080 | 8920
| +105 Deg F |  | 20310 | 18390 | 16620 | 13510 | 12130 | 10860 | 9680 | 8570
| +110 Deg F |  | 19530 | 17690 | 15980 | 12980 | 11650 | 10430
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 15 Lb's | 23.1 Lb's | 5.83 Lb's | 8.63 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.8 | 38 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 21650 | 19590 | 17620 | 13930 | 12200 | 10540 | 8940 | 7390 | 4400 |  |  | 3720
| +95 Deg F |  | 21060 | 19080 | 17150 | 13540 | 11830 | 10190 | 8590 | 7030
| +100 Deg F |  | 20490 | 18560 | 16680 | 13140 | 11450 | 9810 | 8210 | 6640
| +105 Deg F |  | 19910 | 18040 | 16210 | 12720 | 11030 | 9400 | 7800
| +110 Deg F |  | 19330 | 17520 | 15730 | 12270 | 10600 | 8960
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 15.7 Lb's | 24.1 Lb's | 5.8 Lb's | 8.6 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.8 | 38 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O250E4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 21560 | 19430 | 17510 | 14230 | 12790 | 11470 | 10200 | 8970 | 6470 | 5130 |  | 3720
| +95 Deg F |  | 20840 | 18770 | 16900 | 13750 | 12390 | 11140 | 9950 | 8810
| +100 Deg F |  | 20070 | 18060 | 16260 | 13240 | 11960 | 10780 | 9680 | 8620
| +105 Deg F |  | 19260 | 17300 | 15570 | 12680 | 11460 | 10370 | 9350 | 8390
| +110 Deg F |  | 18370 | 16480 | 14800 | 12050 | 10910 | 9890
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS19KAE |  | 2.5 | 2 | 14.3 Lb's | 22.1 Lb's | 5.6 Lb's | 8.23 Lb's | 1/2" | 7/8" | 72 | 207 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 5.8 | 38 | 0.8 | 5 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 33730 | 30480 | 27480 | 22160 | 19830 | 17700 | 15750 | 13980 | 10940 | 9640 |  | 3720
| +95 Deg F |  | 37150 | 33600 | 30320 | 24490 | 21930 | 19590 | 17460 | 15520 | 12150 | 10710
| +100 Deg F |  | 32380 | 29260 | 26370 | 21260 | 19020 | 16970 | 15110 | 13410 | 10500 | 9270
| +105 Deg F |  | 31000 | 28000 | 25240 | 20340 | 18190 | 16230 | 14450 | 12830 | 10060 | 8890
| +110 Deg F |  | 29590 | 26730 | 24080 | 19390 | 17340 | 15480 | 13780 | 12240 | 9610 | 8500
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 20.8 | 112 | 3.1 | 12 | 30 | 30.1 | 50 | 42.1 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 30570 | 27640 | 24960 | 20250 | 18190 | 16290 | 14520 | 12860 | 9780 | 8310 |  | 3720
| +95 Deg F |  | 29550 | 26710 | 24110 | 19540 | 17540 | 15700 | 13990 | 12380
| +100 Deg F |  | 28510 | 25760 | 23250 | 18830 | 16890 | 15110 | 13460 | 11900
| +105 Deg F |  | 27470 | 24810 | 22380 | 18120 | 16240 | 14520 | 12920 | 11420
| +110 Deg F |  | 26420 | 23850 | 21510 | 17400 | 15590 | 13930
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 20.8 | 112 | 3.1 | 12 | 42.1 | 30.1 | 50 | 42.1 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 29790 | 26900 | 24140 | 19010 | 16630 | 14350 | 12150 | 10030 | 5960 |  |  | 3720
| +95 Deg F |  | 29000 | 26190 | 23510 | 18480 | 16130 | 13870 | 11680 | 9550
| +100 Deg F |  | 28200 | 25480 | 22870 | 17930 | 15600 | 13350 | 11170 | 9020
| +105 Deg F |  | 27420 | 24770 | 22220 | 17360 | 15040 | 12790 | 10590
| +110 Deg F |  | 26620 | 24040 | 21550 | 16750 | 14440 | 12180
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 20.8 | 112 | 3.1 | 12 | 42.1 | 30.1 | 50 | 42.1 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 31920 | 28900 | 26060 | 20890 | 18570 | 16400 | 14380 | 12500 | 9130 | 7610 |  | 3720
| +95 Deg F |  | 30910 | 27960 | 25190 | 20120 | 17830 | 15690 | 13700 | 11830
| +100 Deg F |  | 29870 | 26990 | 24280 | 19310 | 17050 | 14940 | 12960 | 11100
| +105 Deg F |  | 28810 | 25990 | 23340 | 18450 | 16210 | 14120 | 12160 | 10310
| +110 Deg F |  | 27700 | 24950 | 22340 | 17530 | 15320 | 13250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 20.8 | 112 | 3.1 | 12 | 42.1 | 30.1 | 50 | 42.1 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 33730 | 30480 | 27480 | 22160 | 19830 | 17700 | 15750 | 13980 | 10940 | 9640 |  | 3720
| +95 Deg F |  | 37150 | 33600 | 30320 | 24490 | 21930 | 19590 | 17460 | 15520 | 12150 | 10710
| +100 Deg F |  | 32380 | 29260 | 26370 | 21260 | 19020 | 16970 | 15110 | 13410 | 10500 | 9270
| +105 Deg F |  | 31000 | 28000 | 25240 | 20340 | 18190 | 16230 | 14450 | 12830 | 10060 | 8890
| +110 Deg F |  | 29590 | 26730 | 24080 | 19390 | 17340 | 15480 | 13780 | 12240 | 9610 | 8500
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 13.7 | 93 | 3.1 | 12 | 25 | 21.2 | 30 | 33.2 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 30570 | 27640 | 24960 | 20250 | 18190 | 16290 | 14520 | 12860 | 9780 | 8310 |  | 3720
| +95 Deg F |  | 29550 | 26710 | 24110 | 19540 | 17540 | 15700 | 13990 | 12380
| +100 Deg F |  | 28510 | 25760 | 23250 | 18830 | 16890 | 15110 | 13460 | 11900
| +105 Deg F |  | 27470 | 24810 | 22380 | 18120 | 16240 | 14520 | 12920 | 11420
| +110 Deg F |  | 26420 | 23850 | 21510 | 17400 | 15590 | 13930
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 13.7 | 93 | 3.1 | 12 | 25 | 21.2 | 30 | 33.2 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 29790 | 26900 | 24140 | 19010 | 16630 | 14350 | 12150 | 10030 | 5960 |  |  | 3720
| +95 Deg F |  | 29000 | 26190 | 23510 | 18480 | 16130 | 13870 | 11680 | 9550
| +100 Deg F |  | 28200 | 25480 | 22870 | 17930 | 15600 | 13350 | 11170 | 9020
| +105 Deg F |  | 27420 | 24770 | 22220 | 17360 | 15040 | 12790 | 10590
| +110 Deg F |  | 26620 | 24040 | 21550 | 16750 | 14440 | 12180
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 13.7 | 93 | 3.1 | 12 | 25 | 21.2 | 30 | 33.2 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 31920 | 28900 | 26060 | 20890 | 18570 | 16400 | 14380 | 12500 | 9130 | 7610 |  | 3720
| +95 Deg F |  | 30910 | 27960 | 25190 | 20120 | 17830 | 15690 | 13700 | 11830
| +100 Deg F |  | 29870 | 26990 | 24280 | 19310 | 17050 | 14940 | 12960 | 11100
| +105 Deg F |  | 28810 | 25990 | 23340 | 18450 | 16210 | 14120 | 12160 | 10310
| +110 Deg F |  | 27700 | 24950 | 22340 | 17530 | 15320 | 13250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 13.7 | 93 | 3.1 | 12 | 25 | 21.2 | 30 | 33.2 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 33730 | 30480 | 27480 | 22160 | 19830 | 17700 | 15750 | 13980 | 10940 | 9640 |  | 3720
| +95 Deg F |  | 37150 | 33600 | 30320 | 24490 | 21930 | 19590 | 17460 | 15520 | 12150 | 10710
| +100 Deg F |  | 32380 | 29260 | 26370 | 21260 | 19020 | 16970 | 15110 | 13410 | 10500 | 9270
| +105 Deg F |  | 31000 | 28000 | 25240 | 20340 | 18190 | 16230 | 14450 | 12830 | 10060 | 8890
| +110 Deg F |  | 29590 | 26730 | 24080 | 19390 | 17340 | 15480 | 13780 | 12240 | 9610 | 8500
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.2 | 48 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 30570 | 27640 | 24960 | 20250 | 18190 | 16290 | 14520 | 12860 | 9780 | 8310 |  | 3720
| +95 Deg F |  | 29550 | 26710 | 24110 | 19540 | 17540 | 15700 | 13990 | 12380
| +100 Deg F |  | 28510 | 25760 | 23250 | 18830 | 16890 | 15110 | 13460 | 11900
| +105 Deg F |  | 27470 | 24810 | 22380 | 18120 | 16240 | 14520 | 12920 | 11420
| +110 Deg F |  | 26420 | 23850 | 21510 | 17400 | 15590 | 13930
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.2 | 48 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 29790 | 26900 | 24140 | 19010 | 16630 | 14350 | 12150 | 10030 | 5960 |  |  | 3720
| +95 Deg F |  | 29000 | 26190 | 23510 | 18480 | 16130 | 13870 | 11680 | 9550
| +100 Deg F |  | 28200 | 25480 | 22870 | 17930 | 15600 | 13350 | 11170 | 9020
| +105 Deg F |  | 27420 | 24770 | 22220 | 17360 | 15040 | 12790 | 10590
| +110 Deg F |  | 26620 | 24040 | 21550 | 16750 | 14440 | 12180
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.2 | 48 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O300E4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 31920 | 28900 | 26060 | 20890 | 18570 | 16400 | 14380 | 12500 | 9130 | 7610 |  | 3720
| +95 Deg F |  | 30910 | 27960 | 25190 | 20120 | 17830 | 15690 | 13700 | 11830
| +100 Deg F |  | 29870 | 26990 | 24280 | 19310 | 17050 | 14940 | 12960 | 11100
| +105 Deg F |  | 28810 | 25990 | 23340 | 18450 | 16210 | 14120 | 12160 | 10310
| +110 Deg F |  | 27700 | 24950 | 22340 | 17530 | 15320 | 13250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS21KAE |  | 3 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 72 | 275 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.2 | 48 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 37150 | 33600 | 30320 | 24490 | 21930 | 19590 | 17460 | 15520 | 12150 | 10710 |  | 3720
| +95 Deg F |  | 35650 | 32240 | 29080 | 23490 | 21030 | 18790 | 16750 | 14890 | 11670 | 10300
| +100 Deg F |  | 34130 | 30850 | 27830 | 22470 | 20110 | 17970 | 16020 | 14240 | 11180 | 9870
| +105 Deg F |  | 30970 | 27990 | 25220 | 20340 | 18210 | 16260 | 14490 | 12890 | 10140 | 8970
| +110 Deg F |  | 28160 | 25420 | 22890 | 18430 | 16470 | 14700 | 13090 | 11630 | 9140 | 8090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 21.2 | 104 | 3.1 | 12 | 30 | 30.6 | 50 | 42.6 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 33770 | 30560 | 27620 | 22440 | 20160 | 18060 | 16110 | 14270 | 10860 | 9240 |  | 3720
| +95 Deg F |  | 32640 | 29520 | 26670 | 21660 | 19450 | 17410 | 15510 | 13740
| +100 Deg F |  | 31490 | 28470 | 25720 | 20870 | 18730 | 16750 | 14920 | 13200
| +105 Deg F |  | 30330 | 27420 | 24750 | 20070 | 18000 | 16100 | 14330 | 12670
| +110 Deg F |  | 29160 | 26350 | 23780 | 19270 | 17280 | 15440
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 21.2 | 104 | 3.1 | 12 | 30 | 30.6 | 50 | 42.6 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 32550 | 29520 | 26660 | 21360 | 18870 | 16460 | 14090 | 11720 | 6960 |  |  | 3720
| +95 Deg F |  | 31650 | 28700 | 25920 | 20730 | 18280 | 15880 | 13510 | 11150
| +100 Deg F |  | 30740 | 27880 | 25170 | 20090 | 17660 | 15270 | 12900 | 10520
| +105 Deg F |  | 29840 | 27060 | 24410 | 19420 | 17000 | 14630 | 12260
| +110 Deg F |  | 28950 | 26240 | 23650 | 18730 | 16340 | 13960
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 21.2 | 104 | 3.1 | 12 | 30 | 30.6 | 50 | 42.6 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 34140 | 30840 | 27810 | 22470 | 20160 | 18070 | 16200 | 14140 | 10320 | 8620 |  | 3720
| +95 Deg F |  | 33020 | 29760 | 26770 | 21550 | 19290 | 17270 | 15460 | 13370
| +100 Deg F |  | 31790 | 28560 | 25620 | 20500 | 18310 | 16350 | 14620 | 12550
| +105 Deg F |  | 30410 | 27230 | 24320 | 19310 | 17170 | 15290 | 13630 | 11660
| +110 Deg F |  | 28860 | 25710 | 22850 | 17940 | 15860 | 14040
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 29.4. Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 21.2 | 104 | 3.1 | 12 | 30 | 30.6 | 50 | 42.6 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 37150 | 33600 | 30320 | 24490 | 21930 | 19590 | 17460 | 15520 | 12150 | 10710 |  | 3720
| +95 Deg F |  | 35650 | 32240 | 29080 | 23490 | 21030 | 18790 | 16750 | 14890 | 11670 | 10300
| +100 Deg F |  | 34130 | 30850 | 27830 | 22470 | 20110 | 17970 | 16020 | 14240 | 11180 | 9870
| +105 Deg F |  | 30970 | 27990 | 25220 | 20340 | 18210 | 16260 | 14490 | 12890 | 10140 | 8970
| +110 Deg F |  | 28160 | 25420 | 22890 | 18430 | 16470 | 14700 | 13090 | 11630 | 9140 | 8090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 13.9 | 93 | 3.1 | 12 | 25 | 21.4 | 35 | 33.4 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 33770 | 30560 | 27620 | 22440 | 20160 | 18060 | 16110 | 14270 | 10860 | 9240 |  | 3720
| +95 Deg F |  | 32640 | 29520 | 26670 | 21660 | 19450 | 17410 | 15510 | 13740
| +100 Deg F |  | 31490 | 28470 | 25720 | 20870 | 18730 | 16750 | 14920 | 13200
| +105 Deg F |  | 30330 | 27420 | 24750 | 20070 | 18000 | 16100 | 14330 | 12670
| +110 Deg F |  | 29160 | 26350 | 23780 | 19270 | 17280 | 15440
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 13.9 | 93 | 3.1 | 12 | 25 | 21.4 | 35 | 33.4 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 32550 | 29520 | 26660 | 21360 | 18870 | 16460 | 14090 | 11720 | 6960 |  |  | 3720
| +95 Deg F |  | 31650 | 28700 | 25920 | 20730 | 18280 | 15880 | 13510 | 11150
| +100 Deg F |  | 30740 | 27880 | 25170 | 20090 | 17660 | 15270 | 12900 | 10520
| +105 Deg F |  | 29840 | 27060 | 24410 | 19420 | 17000 | 14630 | 12260
| +110 Deg F |  | 28950 | 26240 | 23650 | 18730 | 16340 | 13960
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 13.9 | 93 | 3.1 | 12 | 25 | 21.4 | 35 | 33.4 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 34140 | 30840 | 27810 | 22470 | 20160 | 18070 | 16200 | 14140 | 10320 | 8620 |  | 3720
| +95 Deg F |  | 33020 | 29760 | 26770 | 21550 | 19290 | 17270 | 15460 | 13370
| +100 Deg F |  | 31790 | 28560 | 25620 | 20500 | 18310 | 16350 | 14620 | 12550
| +105 Deg F |  | 30410 | 27230 | 24320 | 19310 | 17170 | 15290 | 13630 | 11660
| +110 Deg F |  | 28860 | 25710 | 22850 | 17940 | 15860 | 14040
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 13.9 | 93 | 3.1 | 12 | 25 | 21.4 | 35 | 33.4 | 45
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 37150 | 33600 | 30320 | 24490 | 21930 | 19590 | 17460 | 15520 | 12150 | 10710 |  | 3720
| +95 Deg F |  | 35650 | 32240 | 29080 | 23490 | 21030 | 18790 | 16750 | 14890 | 11670 | 10300
| +100 Deg F |  | 34130 | 30850 | 27830 | 22470 | 20110 | 17970 | 16020 | 14240 | 11180 | 9870
| +105 Deg F |  | 30970 | 27990 | 25220 | 20340 | 18210 | 16260 | 14490 | 12890 | 10140 | 8970
| +110 Deg F |  | 28160 | 25420 | 22890 | 18430 | 16470 | 14700 | 13090 | 11630 | 9140 | 8090
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.2 | 48 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 33770 | 30560 | 27620 | 22440 | 20160 | 18060 | 16110 | 14270 | 10860 | 9240 |  | 3720
| +95 Deg F |  | 32640 | 29520 | 26670 | 21660 | 19450 | 17410 | 15510 | 13740
| +100 Deg F |  | 31490 | 28470 | 25720 | 20870 | 18730 | 16750 | 14920 | 13200
| +105 Deg F |  | 30330 | 27420 | 24750 | 20070 | 18000 | 16100 | 14330 | 12670
| +110 Deg F |  | 29160 | 26350 | 23780 | 19270 | 17280 | 15440
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.2 | 48 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 32550 | 29520 | 26660 | 21360 | 18870 | 16460 | 14090 | 11720 | 6960 |  |  | 3720
| +95 Deg F |  | 31650 | 28700 | 25920 | 20730 | 18280 | 15880 | 13510 | 11150
| +100 Deg F |  | 30740 | 27880 | 25170 | 20090 | 17660 | 15270 | 12900 | 10520
| +105 Deg F |  | 29840 | 27060 | 24410 | 19420 | 17000 | 14630 | 12260
| +110 Deg F |  | 28950 | 26240 | 23650 | 18730 | 16340 | 13960
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.2 | 48 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O350E4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 34140 | 30840 | 27810 | 22470 | 20160 | 18070 | 16200 | 14140 | 10320 | 8620 |  | 3720
| +95 Deg F |  | 33020 | 29760 | 26770 | 21550 | 19290 | 17270 | 15460 | 13370
| +100 Deg F |  | 31790 | 28560 | 25620 | 20500 | 18310 | 16350 | 14620 | 12550
| +105 Deg F |  | 30410 | 27230 | 24320 | 19310 | 17170 | 15290 | 13630 | 11660
| +110 Deg F |  | 28860 | 25710 | 22850 | 17940 | 15860 | 14040
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS26KAE |  | 3.5 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 72 | 293 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 6.2 | 48 | 2.5 | 6 | 15 | 15 | 15 | 19.7 | 20
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 41620 | 37710 | 34070 | 27600 | 24740 | 22120 | 19740 | 17560 | 13790 | 12170 |  | 3720
| +95 Deg F |  | 39920 | 36160 | 32670 | 26450 | 23720 | 21210 | 18920 | 16840 | 13240 | 11700
| +100 Deg F |  | 38190 | 34580 | 31240 | 25290 | 22670 | 20270 | 18090 | 16110 | 12680 | 11210
| +105 Deg F |  | 36420 | 32970 | 29770 | 24100 | 21600 | 19310 | 17240 | 15350 | 12100 | 10710
| +110 Deg F |  | 34610 | 31330 | 28280 | 22870 | 20500 | 18330 | 16350 | 14560 | 11500 | 10180
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 23.4 | 137 | 3.1 | 12 | 30 | 33 | 50 | 45.3 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 37530 | 33990 | 30740 | 25030 | 22500 | 20160 | 17990 | 15950 | 12160 | 10350 |  | 3720
| +95 Deg F |  | 36260 | 32840 | 29680 | 24150 | 21700 | 19430 | 17330 | 15360
| +100 Deg F |  | 34970 | 31660 | 28610 | 23260 | 20890 | 18710 | 16670 | 14760
| +105 Deg F |  | 33680 | 30480 | 27540 | 22370 | 20090 | 17980 | 16010 | 14170
| +110 Deg F |  | 32370 | 29290 | 26460 | 21470 | 19280 | 17250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 23.4 | 137 | 3.1 | 12 | 30 | 33 | 50 | 45.3 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 36510 | 33020 | 29680 | 23460 | 20540 | 17730 | 15030 | 12420 | 7390 |  |  | 3720
| +95 Deg F |  | 35520 | 32150 | 28900 | 22800 | 19920 | 17130 | 14440 | 11830
| +100 Deg F |  | 34540 | 31260 | 28100 | 22120 | 19260 | 16500 | 13810 | 11170
| +105 Deg F |  | 33560 | 30380 | 27290 | 21400 | 18570 | 15810 | 13110
| +110 Deg F |  | 32560 | 29480 | 26460 | 20630 | 17820 | 15060
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 23.4 | 137 | 3.1 | 12 | 30 | 33 | 50 | 45.3 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-DA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 39920 | 36200 | 32690 | 26310 | 23400 | 20680 | 18150 | 15800 | 11560 | 9660 |  | 3720
| +95 Deg F |  | 38640 | 35030 | 31590 | 25330 | 22470 | 19790 | 17290 | 14950
| +100 Deg F |  | 37330 | 33800 | 30440 | 24300 | 21480 | 18840 | 16360 | 14030
| +105 Deg F |  | 35980 | 32540 | 29260 | 23210 | 20430 | 17820 | 15350 | 13040
| +110 Deg F |  | 34570 | 31210 | 28000 | 22040 | 19310 | 16710
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 23.4 | 137 | 3.1 | 12 | 30 | 33 | 50 | 45.3 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 41620 | 37710 | 34070 | 27600 | 24740 | 22120 | 19740 | 17560 | 13790 | 12170 |  | 3720
| +95 Deg F |  | 39920 | 36160 | 32670 | 26450 | 23720 | 21210 | 18920 | 16840 | 13240 | 11700
| +100 Deg F |  | 38190 | 34580 | 31240 | 25290 | 22670 | 20270 | 18090 | 16110 | 12680 | 11210
| +105 Deg F |  | 36420 | 32970 | 29770 | 24100 | 21600 | 19310 | 17240 | 15350 | 12100 | 10710
| +110 Deg F |  | 34610 | 31330 | 28280 | 22870 | 20500 | 18330 | 16350 | 14560 | 11500 | 10180
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 18.4 | 114 | 3.1 | 12 | 30 | 27.1 | 45 | 39.1 | 50
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 37530 | 33990 | 30740 | 25030 | 22500 | 20160 | 17990 | 15950 | 12160 | 10350 |  | 3720
| +95 Deg F |  | 36260 | 32840 | 29680 | 24150 | 21700 | 19430 | 17330 | 15360
| +100 Deg F |  | 34970 | 31660 | 28610 | 23260 | 20890 | 18710 | 16670 | 14760
| +105 Deg F |  | 33680 | 30480 | 27540 | 22370 | 20090 | 17980 | 16010 | 14170
| +110 Deg F |  | 32370 | 29290 | 26460 | 21470 | 19280 | 17250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 18.4 | 114 | 3.1 | 12 | 30 | 27.1 | 45 | 39.1 | 50
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 36510 | 33020 | 29680 | 23460 | 20540 | 17730 | 15030 | 12420 | 7390 |  |  | 3720
| +95 Deg F |  | 35520 | 32150 | 28900 | 22800 | 19920 | 17130 | 14440 | 11830
| +100 Deg F |  | 34540 | 31260 | 28100 | 22120 | 19260 | 16500 | 13810 | 11170
| +105 Deg F |  | 33560 | 30380 | 27290 | 21400 | 18570 | 15810 | 13110
| +110 Deg F |  | 32560 | 29480 | 26460 | 20630 | 17820 | 15060
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 18.4 | 114 | 3.1 | 12 | 30 | 27.1 | 45 | 39.1 | 50
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-EA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 39920 | 36200 | 32690 | 26310 | 23400 | 20680 | 18150 | 15800 | 11560 | 9660 |  | 3720
| +95 Deg F |  | 38640 | 35030 | 31590 | 25330 | 22470 | 19790 | 17290 | 14950
| +100 Deg F |  | 37330 | 33800 | 30440 | 24300 | 21480 | 18840 | 16360 | 14030
| +105 Deg F |  | 35980 | 32540 | 29260 | 23210 | 20430 | 17820 | 15350 | 13040
| +110 Deg F |  | 34570 | 31210 | 28000 | 22040 | 19310 | 16710
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 18.4 | 114 | 3.1 | 12 | 30 | 27.1 | 45 | 39.1 | 50
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 41620 | 37710 | 34070 | 27600 | 24740 | 22120 | 19740 | 17560 | 13790 | 12170 |  | 3720
| +95 Deg F |  | 39920 | 36160 | 32670 | 26450 | 23720 | 21210 | 18920 | 16840 | 13240 | 11700
| +100 Deg F |  | 38190 | 34580 | 31240 | 25290 | 22670 | 20270 | 18090 | 16110 | 12680 | 11210
| +105 Deg F |  | 36420 | 32970 | 29770 | 24100 | 21600 | 19310 | 17240 | 15350 | 12100 | 10710
| +110 Deg F |  | 34610 | 31330 | 28280 | 22870 | 20500 | 18330 | 16350 | 14560 | 11500 | 10180
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8.4 | 58 | 2.5 | 6 | 15 | 15 | 20 | 20 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 37530 | 33990 | 30740 | 25030 | 22500 | 20160 | 17990 | 15950 | 12160 | 10350 |  | 3720
| +95 Deg F |  | 36260 | 32840 | 29680 | 24150 | 21700 | 19430 | 17330 | 15360
| +100 Deg F |  | 34970 | 31660 | 28610 | 23260 | 20890 | 18710 | 16670 | 14760
| +105 Deg F |  | 33680 | 30480 | 27540 | 22370 | 20090 | 17980 | 16010 | 14170
| +110 Deg F |  | 32370 | 29290 | 26460 | 21470 | 19280 | 17250
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8.4 | 58 | 2.5 | 6 | 15 | 15 | 20 | 20 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 36510 | 33020 | 29680 | 23460 | 20540 | 17730 | 15030 | 12420 | 7390 |  |  | 3720
| +95 Deg F |  | 35520 | 32150 | 28900 | 22800 | 19920 | 17130 | 14440 | 11830
| +100 Deg F |  | 34540 | 31260 | 28100 | 22120 | 19260 | 16500 | 13810 | 11170
| +105 Deg F |  | 33560 | 30380 | 27290 | 21400 | 18570 | 15810 | 13110
| +110 Deg F |  | 32560 | 29480 | 26460 | 20630 | 17820 | 15060
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8.4 | 58 | 2.5 | 6 | 15 | 15 | 20 | 20 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O400E4S-GA_R448A_449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 39920 | 36200 | 32690 | 26310 | 23400 | 20680 | 18150 | 15800 | 11560 | 9660 |  | 3720
| +95 Deg F |  | 38640 | 35030 | 31590 | 25330 | 22470 | 19790 | 17290 | 14950
| +100 Deg F |  | 37330 | 33800 | 30440 | 24300 | 21480 | 18840 | 16360 | 14030
| +105 Deg F |  | 35980 | 32540 | 29260 | 23210 | 20430 | 17820 | 15350 | 13040
| +110 Deg F |  | 34570 | 31210 | 28000 | 22040 | 19310 | 16710
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS29KAE |  | 4 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 317 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8.4 | 58 | 2.5 | 6 | 15 | 15 | 20 | 20 | 25
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 47010 | 42490 | 38310 | 30890 | 27640 | 24660 | 21930 | 19460 | 15220 | 13410 |  | 3720
| +95 Deg F |  | 45140 | 40790 | 36760 | 29630 | 26510 | 23650 | 21040 | 18670 | 14620 | 12890
| +100 Deg F |  | 43230 | 39050 | 35190 | 28350 | 25360 | 22630 | 20130 | 17870 | 14010 | 12370
| +105 Deg F |  | 41270 | 37270 | 33580 | 27040 | 24180 | 21580 | 19200 | 17050 | 13380 | 11820
| +110 Deg F |  | 39280 | 35450 | 31930 | 25700 | 22970 | 20490 | 18240 | 16200 | 12720 | 11250
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 23 | 146 | 3.1 | 12 | 30 | 32.8 | 50 | 44.8 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 43300 | 39160 | 35350 | 28690 | 25760 | 23070 | 20560 | 18220 | 13860 | 11770 |  | 3720
| +95 Deg F |  | 41850 | 37840 | 34150 | 27680 | 24850 | 22240 | 19810 | 17540
| +100 Deg F |  | 40390 | 36500 | 32940 | 26670 | 23930 | 21400 | 19050 | 16860
| +105 Deg F |  | 38910 | 35150 | 31710 | 25660 | 23010 | 20570 | 18300 | 16180
| +110 Deg F |  | 37420 | 33790 | 30480 | 24640 | 22090 | 19730
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 23 | 146 | 3.1 | 12 | 30 | 32.8 | 50 | 44.8 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 41100 | 37110 | 33300 | 26230 | 22940 | 19790 | 16760 | 13840 | 8220 |  |  | 3720
| +95 Deg F |  | 40000 | 36140 | 32430 | 25500 | 22250 | 19130 | 16110 | 13180
| +100 Deg F |  | 38910 | 35160 | 31560 | 24740 | 21520 | 18410 | 15390 | 12450
| +105 Deg F |  | 37820 | 34180 | 30660 | 23950 | 20750 | 17650 | 14610
| +110 Deg F |  | 36720 | 33170 | 29730 | 23100 | 19920 | 16810
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 23 | 146 | 3.1 | 12 | 30 | 32.8 | 50 | 44.8 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 44720 | 40500 | 36510 | 29280 | 26010 | 22980 | 20150 | 17520 | 12800 | 10670 |  | 3720
| +95 Deg F |  | 43310 | 39190 | 35290 | 28190 | 24980 | 21990 | 19190 | 16580
| +100 Deg F |  | 41860 | 37840 | 34030 | 27050 | 23890 | 20920 | 18150 | 15560
| +105 Deg F |  | 40360 | 36430 | 32710 | 25850 | 22730 | 19790 | 17040 | 14460
| +110 Deg F |  | 38810 | 34960 | 31320 | 24560 | 21480 | 18560
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 23 | 146 | 3.1 | 12 | 30 | 32.8 | 50 | 44.8 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 47010 | 42490 | 38310 | 30890 | 27640 | 24660 | 21930 | 19460 | 15220 | 13410 |  | 3720
| +95 Deg F |  | 45140 | 40790 | 36760 | 29630 | 26510 | 23650 | 21040 | 18670 | 14620 | 12890
| +100 Deg F |  | 43230 | 39050 | 35190 | 28350 | 25360 | 22630 | 20130 | 17870 | 14010 | 12370
| +105 Deg F |  | 41270 | 37270 | 33580 | 27040 | 24180 | 21580 | 19200 | 17050 | 13380 | 11820
| +110 Deg F |  | 39280 | 35450 | 31930 | 25700 | 22970 | 20490 | 18240 | 16200 | 12720 | 11250
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 20 | 114 | 3.1 | 12 | 30 | 29.1 | 45 | 41.1 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 43300 | 39160 | 35350 | 28690 | 25760 | 23070 | 20560 | 18220 | 13860 | 11770 |  | 3720
| +95 Deg F |  | 41850 | 37840 | 34150 | 27680 | 24850 | 22240 | 19810 | 17540
| +100 Deg F |  | 40390 | 36500 | 32940 | 26670 | 23930 | 21400 | 19050 | 16860
| +105 Deg F |  | 38910 | 35150 | 31710 | 25660 | 23010 | 20570 | 18300 | 16180
| +110 Deg F |  | 37420 | 33790 | 30480 | 24640 | 22090 | 19730
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 20 | 114 | 3.1 | 12 | 30 | 29.1 | 45 | 41.1 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 41100 | 37110 | 33300 | 26230 | 22940 | 19790 | 16760 | 13840 | 8220 |  |  | 3720
| +95 Deg F |  | 40000 | 36140 | 32430 | 25500 | 22250 | 19130 | 16110 | 13180
| +100 Deg F |  | 38910 | 35160 | 31560 | 24740 | 21520 | 18410 | 15390 | 12450
| +105 Deg F |  | 37820 | 34180 | 30660 | 23950 | 20750 | 17650 | 14610
| +110 Deg F |  | 36720 | 33170 | 29730 | 23100 | 19920 | 16810
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 20 | 114 | 3.1 | 12 | 30 | 29.1 | 45 | 41.1 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 44720 | 40500 | 36510 | 29280 | 26010 | 22980 | 20150 | 17520 | 12800 | 10670 |  | 3720
| +95 Deg F |  | 43310 | 39190 | 35290 | 28190 | 24980 | 21990 | 19190 | 16580
| +100 Deg F |  | 41860 | 37840 | 34030 | 27050 | 23890 | 20920 | 18150 | 15560
| +105 Deg F |  | 40360 | 36430 | 32710 | 25850 | 22730 | 19790 | 17040 | 14460
| +110 Deg F |  | 38810 | 34960 | 31320 | 24560 | 21480 | 18560
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 20 | 114 | 3.1 | 12 | 30 | 29.1 | 45 | 41.1 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 47010 | 42490 | 38310 | 30890 | 27640 | 24660 | 21930 | 19460 | 15220 | 13410 |  | 3720
| +95 Deg F |  | 45140 | 40790 | 36760 | 29630 | 26510 | 23650 | 21040 | 18670 | 14620 | 12890
| +100 Deg F |  | 43230 | 39050 | 35190 | 28350 | 25360 | 22630 | 20130 | 17870 | 14010 | 12370
| +105 Deg F |  | 41270 | 37270 | 33580 | 27040 | 24180 | 21580 | 19200 | 17050 | 13380 | 11820
| +110 Deg F |  | 39280 | 35450 | 31930 | 25700 | 22970 | 20490 | 18240 | 16200 | 12720 | 11250
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 9 | 52 | 2.5 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 43300 | 39160 | 35350 | 28690 | 25760 | 23070 | 20560 | 18220 | 13860 | 11770 |  | 3720
| +95 Deg F |  | 41850 | 37840 | 34150 | 27680 | 24850 | 22240 | 19810 | 17540
| +100 Deg F |  | 40390 | 36500 | 32940 | 26670 | 23930 | 21400 | 19050 | 16860
| +105 Deg F |  | 38910 | 35150 | 31710 | 25660 | 23010 | 20570 | 18300 | 16180
| +110 Deg F |  | 37420 | 33790 | 30480 | 24640 | 22090 | 19730
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 9 | 52 | 2.5 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 41100 | 37110 | 33300 | 26230 | 22940 | 19790 | 16760 | 13840 | 8220 |  |  | 3720
| +95 Deg F |  | 40000 | 36140 | 32430 | 25500 | 22250 | 19130 | 16110 | 13180
| +100 Deg F |  | 38910 | 35160 | 31560 | 24740 | 21520 | 18410 | 15390 | 12450
| +105 Deg F |  | 37820 | 34180 | 30660 | 23950 | 20750 | 17650 | 14610
| +110 Deg F |  | 36720 | 33170 | 29730 | 23100 | 19920 | 16810
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 9 | 52 | 2.5 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O450E4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 44720 | 40500 | 36510 | 29280 | 26010 | 22980 | 20150 | 17520 | 12800 | 10670 |  | 3720
| +95 Deg F |  | 43310 | 39190 | 35290 | 28190 | 24980 | 21990 | 19190 | 16580
| +100 Deg F |  | 41860 | 37840 | 34030 | 27050 | 23890 | 20920 | 18150 | 15560
| +105 Deg F |  | 40360 | 36430 | 32710 | 25850 | 22730 | 19790 | 17040 | 14460
| +110 Deg F |  | 38810 | 34960 | 31320 | 24560 | 21480 | 18560
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS33KAE |  | 4.5 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 338 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 9 | 52 | 2.5 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-DA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 51190 | 46660 | 42420 | 34800 | 31400 | 28260 | 25360 | 22680 | 17950 | 15880 |  | 3720
| +95 Deg F |  | 49080 | 44710 | 40630 | 33310 | 30050 | 27030 | 24260 | 21700 | 17190 | 15230
| +100 Deg F |  | 46940 | 42740 | 38820 | 31800 | 28670 | 25790 | 23140 | 20700 | 16410 | 14540
| +105 Deg F |  | 44770 | 40750 | 36990 | 30270 | 27280 | 24520 | 21990 | 19680 | 15600 | 13830
| +110 Deg F |  | 42590 | 38740 | 35140 | 28710 | 25860 | 23240 | 20830 | 18630 | 14770 | 13100
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 28.5 | 169 | 3.1 | 12 | 30 | 39.7 | 60 | 51.7 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-DA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 42520 | 39780 | 36960 | 31220 | 28380 | 25620 | 22960 | 20430 | 15900 | 13960 |  | 3720
| +95 Deg F |  | 41400 | 38720 | 35960 | 30360 | 27590 | 24900 | 22300 | 19830
| +100 Deg F |  | 40260 | 37640 | 34950 | 29490 | 26790 | 24150 | 21620 | 19220
| +105 Deg F |  | 39120 | 36550 | 33930 | 28600 | 25970 | 23400 | 20940 | 18600
| +110 Deg F |  | 37950 | 35450 | 32890 | 27700 | 25140 | 22640
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 28.5 | 169 | 3.1 | 12 | 30 | 39.7 | 60 | 51.7 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-DA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 42410 | 39680 | 36870 | 31140 | 28310 | 25560 | 22900 | 20380 | 15860 |  |  | 3720
| +95 Deg F |  | 41300 | 38620 | 35870 | 30280 | 27520 | 24840 | 22240 | 19780
| +100 Deg F |  | 40160 | 37550 | 34860 | 29420 | 26720 | 24090 | 21570 | 19170
| +105 Deg F |  | 39020 | 36460 | 33850 | 28530 | 25910 | 23340 | 20890
| +110 Deg F |  | 37860 | 35360 | 32810 | 27630 | 25080 | 22580
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 28.5 | 169 | 3.1 | 12 | 30 | 39.7 | 60 | 51.7 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-DA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 43500 | 40740 | 37960 | 32460 | 29780 | 27180 | 24660 | 22230 | 17670 | 15540 |  | 3720
| +95 Deg F |  | 42130 | 39,,60 | 36770 | 31460 | 28870 | 26370 | 23930 | 21570
| +100 Deg F |  | 40720 | 38130 | 35540 | 30430 | 27930 | 25500 | 23140 | 20870
| +105 Deg F |  | 39245 | 36745 | 34250 | 29320 | 26915 | 24575 | 21520 | 19409
| +110 Deg F |  | 37770 | 35360 | 32960 | 28210 | 25900 | 23650
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 1 | 60 | 28.5 | 169 | 3.1 | 12 | 30 | 39.7 | 60 | 51.7 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 51190 | 46660 | 42420 | 34800 | 31400 | 28260 | 25360 | 22680 | 17950 | 15880 |  | 3720
| +95 Deg F |  | 49080 | 44710 | 40630 | 33310 | 30050 | 27030 | 24260 | 21700 | 17190 | 15230
| +100 Deg F |  | 46940 | 42740 | 38820 | 31800 | 28670 | 25790 | 23140 | 20700 | 16410 | 14540
| +105 Deg F |  | 44770 | 40750 | 36990 | 30270 | 27280 | 24520 | 21990 | 19680 | 15600 | 13830
| +110 Deg F |  | 42590 | 38740 | 35140 | 28710 | 25860 | 23240 | 20830 | 18630 | 14770 | 13100
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 19.2 | 123 | 3.1 | 12 | 30 | 28.1 | 45 | 40.1 | 50
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 42520 | 39780 | 36960 | 31220 | 28380 | 25620 | 22960 | 20430 | 15900 | 13960 |  | 3720
| +95 Deg F |  | 41400 | 38720 | 35960 | 30360 | 27590 | 24900 | 22300 | 19830
| +100 Deg F |  | 40260 | 37640 | 34950 | 29490 | 26790 | 24150 | 21620 | 19220
| +105 Deg F |  | 39120 | 36550 | 33930 | 28600 | 25970 | 23400 | 20940 | 18600
| +110 Deg F |  | 37950 | 35450 | 32890 | 27700 | 25140 | 22640
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 19.2 | 123 | 3.1 | 12 | 30 | 28.1 | 45 | 40.1 | 50
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 42410 | 39680 | 36870 | 31140 | 28310 | 25560 | 22900 | 20380 | 15860 |  |  | 3720
| +95 Deg F |  | 41300 | 38620 | 35870 | 30280 | 27520 | 24840 | 22240 | 19780
| +100 Deg F |  | 40160 | 37550 | 34860 | 29420 | 26720 | 24090 | 21570 | 19170
| +105 Deg F |  | 39020 | 36460 | 33850 | 28530 | 25910 | 23340 | 20890
| +110 Deg F |  | 37860 | 35360 | 32810 | 27630 | 25080 | 22580
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 19.2 | 123 | 3.1 | 12 | 30 | 28.1 | 45 | 40.1 | 50
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 43500 | 40740 | 37960 | 32460 | 29780 | 27180 | 24660 | 22230 | 17670 | 15540 |  | 3720
| +95 Deg F |  | 42130 | 39,,60 | 36770 | 31460 | 28870 | 26370 | 23930 | 21570
| +100 Deg F |  | 40720 | 38130 | 35540 | 30430 | 27930 | 25500 | 23140 | 20870
| +105 Deg F |  | 39245 | 36745 | 34250 | 29320 | 26915 | 24575 | 21520 | 19409
| +110 Deg F |  | 37770 | 35360 | 32960 | 28210 | 25900 | 23650
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 19.2 | 123 | 3.1 | 12 | 30 | 28.1 | 45 | 40.1 | 50
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-GA-R404
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 51190 | 46660 | 42420 | 34800 | 31400 | 28260 | 25360 | 22680 | 17950 | 15880 |  | 3720
| +95 Deg F |  | 49080 | 44710 | 40630 | 33310 | 30050 | 27030 | 24260 | 21700 | 17190 | 15230
| +100 Deg F |  | 46940 | 42740 | 38820 | 31800 | 28670 | 25790 | 23140 | 20700 | 16410 | 14540
| +105 Deg F |  | 44770 | 40750 | 36990 | 30270 | 27280 | 24520 | 21990 | 19680 | 15600 | 13830
| +110 Deg F |  | 42590 | 38740 | 35140 | 28710 | 25860 | 23240 | 20830 | 18630 | 14770 | 13100
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8.7 | 62 | 2.5 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 42520 | 39780 | 36960 | 31220 | 28380 | 25620 | 22960 | 20430 | 15900 | 13960 |  | 3720
| +95 Deg F |  | 41400 | 38720 | 35960 | 30360 | 27590 | 24900 | 22300 | 19830
| +100 Deg F |  | 40260 | 37640 | 34950 | 29490 | 26790 | 24150 | 21620 | 19220
| +105 Deg F |  | 39120 | 36550 | 33930 | 28600 | 25970 | 23400 | 20940 | 18600
| +110 Deg F |  | 37950 | 35450 | 32890 | 27700 | 25140 | 22640
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8.7 | 62 | 2.5 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 42410 | 39680 | 36870 | 31140 | 28310 | 25560 | 22900 | 20380 | 15860 |  |  | 3720
| +95 Deg F |  | 41300 | 38620 | 35870 | 30280 | 27520 | 24840 | 22240 | 19780
| +100 Deg F |  | 40160 | 37550 | 34860 | 29420 | 26720 | 24090 | 21570 | 19170
| +105 Deg F |  | 39020 | 36460 | 33850 | 28530 | 25910 | 23340 | 20890
| +110 Deg F |  | 37860 | 35360 | 32810 | 27630 | 25080 | 22580
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8.7 | 62 | 2.5 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O500E4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 43500 | 40740 | 37960 | 32460 | 29780 | 27180 | 24660 | 22230 | 17670 | 15540 |  | 3720
| +95 Deg F |  | 42130 | 39,,60 | 36770 | 31460 | 28870 | 26370 | 23930 | 21570
| +100 Deg F |  | 40720 | 38130 | 35540 | 30430 | 27930 | 25500 | 23140 | 20870
| +105 Deg F |  | 39245 | 36745 | 34250 | 29320 | 26915 | 24575 | 21520 | 19409
| +110 Deg F |  | 37770 | 35360 | 32960 | 28210 | 25900 | 23650
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS38K4E |  | 5 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 74 | 345 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 8.7 | 62 | 2.5 | 6 | 20 | 15 | 20 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O600E4S-EA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 60890 | 55630 | 50700 | 41850 | 37900 | 34240 | 30850 | 27730 | 22150 | 19660 |  | 3720
| +95 Deg F |  | 58360 | 53280 | 48530 | 40030 | 36240 | 32730 | 29500 | 26520 | 21230 | 18880
| +100 Deg F |  | 55780 | 50900 | 46350 | 38200 | 34570 | 31220 | 28130 | 25300 | 20290 | 18070
| +105 Deg F |  | 53200 | 48500 | 44150 | 36340 | 32880 | 29690 | 26750 | 24060 | 19330 | 17240
| +110 Deg F |  | 50560 | 46090 | 41930 | 34480 | 31170 | 28140 | 25360 | 22810 | 18340 | 16390
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS45K4E |  | 6 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 76 | 365 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 21.5 | 156 | 3.1 | 12 | 30 | 30.9 | 50 | 42.9 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O600E4S-EA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 51310 | 47590 | 43900 | 36680 | 33220 | 29890 | 26730 | 23770 | 18550 | 16330 |  | 3720
| +95 Deg F |  | 50080 | 46430 | 42810 | 35750 | 32360 | 29100 | 26010 | 23120
| +100 Deg F |  | 48840 | 45270 | 41720 | 34810 | 31490 | 28310 | 25280 | 22450
| +105 Deg F |  | 47590 | 44080 | 40610 | 33850 | 30610 | 27500 | 24540 | 21770
| +110 Deg F |  | 46310 | 42880 | 39480 | 32880 | 29710 | 26670
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS45K4E |  | 6 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 76 | 365 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 21.5 | 156 | 3.1 | 12 | 30 | 30.9 | 50 | 42.9 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O600E4S-EA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 51180 | 47470 | 43790 | 36590 | 33140 | 29820 | 26660 | 23710 | 18500 |  |  | 3720
| +95 Deg F |  | 49960 | 46310 | 42700 | 35660 | 32280 | 29030 | 25950 | 23060
| +100 Deg F |  | 48720 | 45160 | 41620 | 34720 | 31410 | 28240 | 25220 | 22390
| +105 Deg F |  | 47470 | 43970 | 40510 | 33770 | 30530 | 27430 | 24480
| +110 Deg F |  | 46200 | 42770 | 39380 | 32800 | 29640 | 26600
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS45K4E |  | 6 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 76 | 365 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 21.5 | 156 | 3.1 | 12 | 30 | 30.9 | 50 | 42.9 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O600E4S-EA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 52450 | 48680 | 45020 | 38040 | 34750 | 31600 | 28610 | 25790 | 20640 | 18310 |  | 3720
| +95 Deg F |  | 50910 | 47250 | 43700 | 36940 | 33760 | 30710 | 27810 | 25080
| +100 Deg F |  | 49,330 | 45790 | 42350 | 35820 | 32730 | 29790 | 26980 | 24330
| +105 Deg F |  | 48510 | 44255 | 40930 | 34625 | 31645 | 28805 | 25008 | 22627
| +110 Deg F |  | 46050 | 42720 | 39510 | 33430 | 30560 | 27820
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS45K4E |  | 6 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 76 | 365 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 208/230 | 3 | 60 | 21.5 | 156 | 3.1 | 12 | 30 | 30.9 | 50 | 42.9 | 60
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O600E4S-GA_R404A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R404A / R507
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 60890 | 55630 | 50700 | 41850 | 37900 | 34240 | 30850 | 27730 | 22150 | 19660 |  | 3720
| +95 Deg F |  | 58360 | 53280 | 48530 | 40030 | 36240 | 32730 | 29500 | 26520 | 21230 | 18880
| +100 Deg F |  | 55780 | 50900 | 46350 | 38200 | 34570 | 31220 | 28130 | 25300 | 20290 | 18070
| +105 Deg F |  | 53200 | 48500 | 44150 | 36340 | 32880 | 29690 | 26750 | 24060 | 19330 | 17240
| +110 Deg F |  | 50560 | 46090 | 41930 | 34480 | 31170 | 28140 | 25360 | 22810 | 18340 | 16390
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS45K4E |  | 6 | 1 | 28 Lb's | 37.9 Lb's | 11 Lb's | 15 Lb's | 5/8" | 1-1/8" | 76 | 365 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 10.3 | 75 | 2.5 | 6 | 20 | 16.3 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O600E4S-GA_R407A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 51310 | 47590 | 43900 | 36680 | 33220 | 29890 | 26730 | 23770 | 18550 | 16330 |  | 3720
| +95 Deg F |  | 50080 | 46430 | 42810 | 35750 | 32360 | 29100 | 26010 | 23120
| +100 Deg F |  | 48840 | 45270 | 41720 | 34810 | 31490 | 28310 | 25280 | 22450
| +105 Deg F |  | 47590 | 44080 | 40610 | 33850 | 30610 | 27500 | 24540 | 21770
| +110 Deg F |  | 46310 | 42880 | 39480 | 32880 | 29710 | 26670
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS45K4E |  | 6 | 1 | 30.9 Lb's | 41.8 Lb's | 12 Lb's | 16.6 Lb's | 5/8" | 1-1/8" | 76 | 365 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 10.3 | 75 | 2.5 | 6 | 20 | 16.3 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O600E4S-GA_R407C
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R407C
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 51180 | 47470 | 43790 | 36590 | 33140 | 29820 | 26660 | 23710 | 18500 |  |  | 3720
| +95 Deg F |  | 49960 | 46310 | 42700 | 35660 | 32280 | 29030 | 25950 | 23060
| +100 Deg F |  | 48720 | 45160 | 41620 | 34720 | 31410 | 28240 | 25220 | 22390
| +105 Deg F |  | 47470 | 43970 | 40510 | 33770 | 30530 | 27430 | 24480
| +110 Deg F |  | 46200 | 42770 | 39380 | 32800 | 29640 | 26600
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS45K4E |  | 6 | 1 | 32.3 Lb's | 43.7 Lb's | 12 Lb's | 16.5 Lb's | 5/8" | 1-1/8" | 76 | 365 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 10.3 | 75 | 2.5 | 6 | 20 | 16.3 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A

## R_O600E4S-GA_R448A_R449A
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC | [5 empty] | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 | [5 empty] | R Series - Model RBO / RFO
|  |  |  | Duluth, GA 30096 | [5 empty] | Air Cooled Condensing Unit
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [6 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [6 empty] | For Approval
Job Name: | [6 empty] | Job Location:
Customer Name: | [6 empty] | Order Number:
Architect / Engineer: | [6 empty] | Prepared By:
Unit Model Number: | [6 empty] | Tagging Info:
Unit Quantity: | [6 empty] | Date: |  |  | 2016-05-12 14:49
| Outdoor |  | CAPACITY DATA (BTUH) / R448A / R449A
| Ambient |  | Saturated Suction Temperature (SST)
| Temperature |  | +30 F | +25 F | +20 F | +10 F | +5 F | 0 F | -5 F | -10 F | -20 F | -25 F
| +90 Deg F |  | 52450 | 48680 | 45020 | 38040 | 34750 | 31600 | 28610 | 25790 | 20640 | 18310 |  | 3720
| +95 Deg F |  | 50910 | 47250 | 43700 | 36940 | 33760 | 30710 | 27810 | 25080
| +100 Deg F |  | 49330 | 45790 | 42350 | 35820 | 32730 | 29790 | 26980 | 24330
| +105 Deg F |  | 48510 | 44255 | 40930 | 34625 | 31645 | 28805 | 25008 | 22627
| +110 Deg F |  | 46050 | 42720 | 39510 | 33430 | 30560 | 27820
Note: Maximum operating suction superheat at compressor must not exceed 20 degrees in shaded areas
PHYSICAL DATA
Compressor |  | Compressor |  | Unit | Fan | Std Rcvr | OS Rcvr | Summer | Winter | Refrig Conn (ODS) |  | Sound | Net
Type |  | Model # |  | HP | Qty | Cap (90%) | Cap (90%) | Charge | Charge + | Liquid | Suction | dBA * | Weight
Scroll |  | ZS45K4E |  | 6 | 1 | 29.4 Lb's | 39.8 Lb's | 11.5 Lb's | 15.8 Lb's | 5/8" | 1-1/8" | 76 | 365 Lb's
ELECTRICAL DATA
| Voltage Characteristics |  |  | Compressor |  | Cond Fan | Max Evap | Max Def | Air Defrost ** |  | Electric Defrost **
| Volts | Phase | Hertz | RLA | LRA | FLA | Fan Amps | Htr Amps | MCA | MOPD | MCA | MOPD
| 460 | 3 | 60 | 10.3 | 75 | 2.5 | 6 | 20 | 16.3 | 25 | 26 | 30
Notes: | + Applies to flooded head pressure control units only (model RFO) with standard receiver option
* Estimated operating sound pressure value (dBA) measured 10' from the unit air discharge
** The MCA and MOPD values include an allowance of (1) amp for the control circuit
Additional Comments:
R_SBMTL_1115-A