Catalog No.:	2100.91A

Effective:	05/31/19

Replaces:	05/01/15

XPAK FT® TYPE H - MODELS 088AR-398A
SUGGESTED SPECIFICATIONS

### DIVISION 23 52 33.13

### WALL-HUNG FIRE-TUBE STAINLESS STEEL HEATING BOILERS

- - GENERAL

  - SUMMARY

    - Section includes wall-hung condensing gas-fired, stainless steel, hydronic heating boilers

Specifier Note:  Use as needed

    - Related Sections

      - Building Services Piping – Division 23 21 00

      - Breeching, Chimneys, and Stacks (Venting) – Division 23 51 00

      - HVAC Instrumentation and Controls – Division 23 09 00

      - Electrical – Division 23 09 33

  - REFERENCES

    - ANSI Z21.13/CSA 4.9

    - ASME, Section IV

    - 2006 UMC, Section 1107.6

    - ANSI/ASHRAE 15-1994, Section 8.13.6

    - National Fuel Gas Code, ANSI Z223.1/NFPA 54

    - NEC, ANSI/NFPA 70

    - ISO 9001:2015

  - SUBMITTALS

    - Product data sheet (including dimensions, rated capacities, shipping weights, accessories)

    - Wiring diagram

    - Warranty information

    - Installation and operating instructions

  - QUALITY ASSURANCE

    - Regulatory Requirements

      - ANSI Z21.13/CSA 4.9

      - Local and national air quality regulations for low NOx boilers

    - Certifications

      - CSA

      - ASME, Section IV, H Stamp and National Board Listed

      - S.C.A.Q.M.D. Rule 1146.2 (<14 ng/J NOx emissions @ 3% O2)

      - CSA Low Lead Certified – less than .25% Lead

  - Heat Exchanger WARRANTY

    - Limited one-year parts warranty

    - Limited ten-year closed-system heat exchanger warranty

    - Limited twenty-year thermal shock warranty

- - PRODUCTS

  - MANUFACTURER

    - Raypak, Inc.

      - Contact: 2151 Eastman Ave., Oxnard, CA 93030; Telephone: (805) 278-5300; 
Fax: (800) 872-9725; Web site: www.raypak.com

      - Product: XPak FT® wall-hung condensing stainless steel hydronic heating boiler(s)

  - BOILERS

    - General

      - The boiler(s) shall be fired with                    gas at a rated input of                      BTU/hr.

      - The boiler(s) shall be CSA tested and certified with a minimum AFUE rating of 94.8 percent at full fire for models 88AR-298AR, or minimum thermal efficiency of 96% for model 398A.

      - The boiler(s) shall be ASME inspected and stamped and National Board registered for 80 PSIG maximum allowable working pressure and 192ºF maximum allowable temperature, complete with a Manufacturer's Data Report.

      - The wall-hung boiler(s) shall have a total weight of 275 lbs. or less.

    - Primary Heat Exchanger

      - The primary heat exchanger shall be of a single-pass flue gas, vertically oriented fire-tube design with water surrounding the combustion chamber for maximum efficiency.

      - The heat exchanger shall be fully welded construction utilizing 316L stainless steel for the fire-tubes, tube sheets, combustion chamber, flue collector and pressure vessel shell.

      - The low water volume primary heat exchanger shall carry a twenty-year warranty against thermal shock.

      - The flue connection and combustion air opening shall be located on the top of the unit.  The, gas connection, water connections, condensate drain and electrical connections shall be located on the bottom of the unit.

    - Condensate Drain

      - The boiler(s) will incorporate a condensate drain.

    - Burner

      - The combustion chamber shall be of the sealed-combustion type employing a high-temperature metal fiber burner, mounted in a vertical orientation.

      - The burner shall be a premix design and constructed of high-grade stainless steel and must be capable of firing at both a complete blue flame with maximum gas and air input as well as firing infrared when gas and air are reduced. The burner must be capable of firing at 100% of rated input when supplied with 4.0” WC of inlet gas pressure, so as to maintain service under heavy demand conditions; no exceptions.

      - The burner shall use a combustion air blower to precisely control the fuel/air mixture for maximum efficiency throughout the entire range of modulation. The combustion air blower shall operate for a pre-purge period before burner ignition and a post-purge period after burner operation to clear the combustion chamber.

      - The blower shall infinitely vary its output in response to a PWM signal supplied directly from the Versa IC® modulating control, thereby electronically and precisely adjusting the volume of air and gas supplied for combustion. Minimum fire shall be 20 percent of rated input for models 88AR-278AR, and 10% for model 398A.

    - Ignition System

      - The boiler(s) shall be equipped with a 100 percent safety shutdown.

      - The ignition shall be spark ignition type with full flame rectification by the ignition source, with a three try-for-ignition sequence, to ensure consistent operation.

      - The igniter will be located alongside the burner to ensure easy ignition.

      - The Versa IC control module shall include an LCD display that indicates individual diagnostic faults.

      - A viewing port shall be provided, permitting visual observation of burner operation.

    - Gas Train

      - The boiler(s) shall have dual-seated main gas valve.

      - Gas control trains shall have a redundant safety shut-off feature, main gas regulation, and plugged pressure tapping to meet the requirements of ANSI Z21.13/CSA 4.9.

    - Boiler Control

      - The following safety controls shall be provided:

        - 195°F high limit control with manual reset (maximum system setpoint 190°F)

        - Flow switch, shipped loose (optional on all models)

        - 30 PSIG ASME pressure relief valve, piped by the installer to an approved drain (shipped loose)

        - Temperature and pressure gauge (shipped loose)

      - The boiler(s) shall be equipped with an integrated PID modulating temperature controller with LCD display that incorporates an adjustable energy-saving pump control relay and freeze protection and is factory mounted and wired to improve system efficiency; three water sensors are included (system sensor is loose).

      - The boiler(s) shall allow for 0-10 VDC input connection for remote building DDC system control of system temperature or firing rate and have a built-in “Cascade” function to sequence and rotate while maintaining modulation of up to four boilers without utilizing an external sequencer.

    - Firing Mode: Provide electronic modulating control of the gas input to the boiler.

    - Boiler Diagnostics

      - Provide monitoring of all safeties, internal/external interlocks with fault display by a 3-1/2” LCD display:

        - System status

        - Ignition failure

        - Condensate blockage

        - Blower speed error

        - Low 24VAC

        - Manual reset high limit

        - Low Water Cut Off (LWCO) (LWCO with test button standard on all sizes; LWCO with test & reset buttons standard on model 398A only)

        - Blocked vent

        - Low gas pressure switch (field-installed option)

        - High gas pressure switch (field-installed option on models 198AR-398A only.)

        - Flow switch fault (field-installed option)

        - Sensor failure

      - Inlet sensor (open or short)

      - Outlet sensor (open or short)

      - System sensor (open or short)

      - Air sensor (optional) (open or short)

      - DHW sensor (optional) (open or short)

        - High vent temperature

        - Internal control fault

        - ID Card fault

        - Cascade communication error

    - Cabinet

      - The corrosion-resistant galvanized-steel jackets shall be finished with a baked-on epoxy powder coat, applied prior to assembly for complete coverage.

      - The boiler(s), if located on a combustible wall, shall not require a separate combustible wall panel.

      - The boiler(s) shall connect both the combustion air and flue products through the top of the unit.

    - Boiler Pump – An optional field-installed pump system shall be available.

  - BOILER OPERATING CONTROLS

    - Each boiler shall have the ability to receive a 0-10 VDC signal from the Central Energy Management and Direct Digital Control System (EMCS) to vary the setpoint or control firing rate. Each boiler shall have an alarm contact for connection to the central EMCS system.

    - Each boiler shall be equipped with Modbus communications compatibility with up to 146 points of data available.

    - The boiler(s) shall feature the integrated VERSA IC modulating digital controller with 3 user-selectable modes, mounted and wired.

      - Mode 1 = Hydronic, without indirect domestic hot water.

      - Mode 2 = Hydronic, with indirect domestic hot water plumbed into system loop piping

      - Mode 3 = Hydronic, with indirect domestic hot water plumbed into boiler loop plumbing

    - System sensor and optional air temperature sensor shall be shipped loose for field installation by installing contractor. Inlet/Outlet sensors are factory-installed.

    - VERSA IC control system is capable of controlling up to 3 connected pumps.

      - Boiler pump

      - System pump

      - Indirect DHW pump

  - DIRECT VENT

    - The boiler(s) shall meet safety standards for direct vent equipment as noted by the 2006 Uniform Mechanical Code, section 1107.6, and ASHRAE 15-1994, section 8.13.6.

    - The boiler shall be capable of supporting up to 100 ft. of combustion air duct and up to 100 ft. of effective vent length without reduction of vent size.

  - SOURCE QUALITY CONTROL

    - The boiler(s) shall be completely assembled, wired, and fire-tested prior to shipment from the factory.

    - The boiler(s) shall be furnished with the sales order, ASME Manufacturer’s Data Report(s), inspection sheet, wiring diagram, rating plate and Installation and Operating Manual.

- - EXECUTION

  - INSTALLATION

    - Must comply with:

      - Local, state, provincial, and national codes, laws, regulations and ordinances

      - National Fuel Gas Code, ANSI Z223.1/NFPA 54 – latest edition

      - National Electrical Code, ANSI/NFPA 70 – latest edition

      - Canada only: CAN/CSA B149 Installation Code and CSA C22.1 CEC Part I

      - Manufacturer’s installation instructions, including required service clearances and venting guidelines

    - Manufacturer’s representative to verify proper and complete installation.

  - START-UP

    - Shall be performed by Raypak factory-trained personnel.

    - Test during operation and adjust if necessary:

      - Safeties

      - Operating controls

      - Static and full load gas supply pressure

      - Gas manifold and blower suction pressure

      - Combustion analysis

    - Submit copy of start-up report to Architect and Engineer.

  - training

    - Provide factory-authorized service representative to train maintenance personnel on procedures and schedules related to start-up, shut-down, troubleshooting, servicing, and preventive maintenance.

    - Schedule training at least seven days in advance.

- END OF SECTION