## SA_SUB_INDEX
|  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  | SUBMITTAL DATA INDEX
|  | 3885 Crestwood Parkway / Suite 500 |  |  | Model Series / Super-Flo (Rev C)
|  | Duluth, GA 30096 |  |  | SA - Air Defrost
(P) 800-288-9488 / (F) 256-259-7478
|  | http://witt.htpgusa.com |  |  | Low Profile Unit Cooler
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
SUBMITTAL DATA INDEX
|  | 8 FPI | 6 FPI | 4 FPI
|  | MODELS | MODELS | MODELS
|  | SA18-41C-* ^ | SA16-39C-* ^ | SA14-42C-* ^
|  | SA18-53C-* ^ | SA16-48C-* ^ | SA24-84C-* ^
|  | SA18-66C-* ^ | SA16-58C-* ^ | SA24-105C-* ^
|  | SA28-76C-* ^ | SA26-70C-* ^ | SA34-130C-* ^
|  | SA28-97C-* ^ | SA26-87C-*-^ | SA44-170C-* ^
|  | SA28-106C-* ^ | SA26-115C-* ^ | SA54-215C-* ^
|  | SA28-122C-* ^ | SA36-145C-* ^ | SA64-255C-* ^
|  | SA28-134C-* ^ | SA36-170C-* ^
|  | SA38-160C-* ^ | SA46-192C-* ^
|  | SA38-195C-* ^ | SA46-230C-* ^
|  | SA48-212C-* ^ | SA56-245C-* ^
|  | SA48-264C-* ^ | SA66-295C-* ^
|  | SA58-275C-* ^ | SA66-345C-* ^
SA68-318C-* ^
SA68-390C-* ^
S A 1 8 - 41 C - * ^ +
Pre-Assembly Code
| Super-Flo |  |  |  | See Product Catalog
Features / Configurations
[5 empty] | Motor Type |  | 3720
| Air Defrost |  |  |  | P = PSC
E = ECM
| Number of Fans |  |  |  | Voltage Code
A = 115/1
D = 208/230/1
F = 460/1
Fins Per Inch
Revison Code
BTUH in Hundreds
SA_SUB_INDEX_0216-A

## SA_1 FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Super-Flo - Model SA (Rev C)
|  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost Unit Cooler
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2016-02-16 21:08
| CAPACITY (BTUH) @ +25 DEG F SST |  |  |  |  | FAN DATA
| REFRIGERANT R-404A |  |  |  |  | Qty | Fan | CFM | Air Throw | Air Throw
| Unit Model |  | 10 TD | 12 TD |  | Fans | Diameter |  | Std Guard | Hi-Throw
| SA18-41C-* ^ |  | 4100 | 4900 |  | 1 | 12' | 800 | 15' | 20'
| SA18-53C-* ^ |  | 5300 | 6400 |  | 1 | 12" | 770 | 15' | 20'
| SA18-66C-* ^ |  | 6600 | 7900 |  | 1 | 12" | 740 | 15' | 20'
| SA16-39C-* ^ |  | 3900 | 4700 |  | 1 | 12" | 830 | 15' | 20'
| SA16-48C-* ^ |  | 4800 | 5800 |  | 1 | 12" | 800 | 15' | 20'
| SA16-58C-* ^ |  | 5800 | 7000 |  | 1 | 12" | 780 | 15' | 20'
| SA14-42C-* ^ |  | 4200 | 5000 |  | 1 | 12" | 830 | 15' | 20'
PHYSICAL DATA
| Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net
| Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight
| SA18-41C-* ^ |  | 8 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 0.7 Lb's | 30 Lb's
| SA18-53C-* ^ |  | 8 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 1.1 Lb's | 31 Lb's
| SA18-66C-* ^ |  | 8 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 1.5 Lb's | 33 Lb's
| SA16-39C-* ^ |  | 6 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 0.7 Lb's | 37 Lb's
| SA16-48C-* ^ |  | 6 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 1.1 Lb's | 40 Lb's
| SA16-58C-* ^ |  | 6 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 1.5 Lb's | 43 Lb's
| SA14-42C-* ^ |  | 4 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 1.1 Lb's | 41 Lb's
ELECTRICAL DATA
|  | Voltage | Phase | Hertz | PSC Mtr | EC Mtr | Total Motor Amps |  | Voltage
[5 empty] | Amps Ea | Amps Ea | PSC | EC | Code
|  | 115 | 1 | 60 | 1 | 0.9 | 1 | 0.9 | A
|  | 208/230 | 1 | 60 | 0.5 | 0.45 | 0.5 | 0.45 | D
|  | 460 | 1 | 60 | N/A | N/A | 0.54 | N/A | F
Notes: | The first * in the listed model numbers designates the unit voltage; A = 115, D = 208/230
The ^ in the listed model numbers designates the unit motor type; P = Perm Split Cap; EC = Electronically Comm
Additional Comments:
SA_SBMTL_0216-A

## SA_2 FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Super-Flo - Model SA (Rev C)
|  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost Unit Cooler
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2016-02-16 21:08
| CAPACITY (BTUH) @ +25 DEG F SST |  |  |  |  | FAN DATA
| REFRIGERANT R-404A |  |  |  |  | Qty | Fan | CFM | Air Throw | Air Throw
| Unit Model |  | 10 TD | 12 TD |  | Fans | Diameter |  | Std Guard | Hi-Throw
| SA28-76C-* ^ |  | 7600 | 9100 |  | 2 | 12' | 1460 | 15' | 20'
| SA28-97C-* ^ |  | 9700 | 11600 |  | 2 | 12" | 1420 | 15' | 20'
| SA28-122C-* ^ |  | 12200 | 14600 |  | 2 | 12" | 1380 | 15' | 20'
| SA26-70C-* ^ |  | 7000 | 8400 |  | 2 | 12" | 1540 | 15' | 20'
| SA26-87C-* ^ |  | 8700 | 10400 |  | 2 | 12" | 1500 | 15' | 20'
PHYSICAL DATA
| Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net
| Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight
| SA28-76C-* ^ |  | 8 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 1.2 Lb's | 43 Lb's
| SA28-97C-* ^ |  | 8 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 1.8 Lb's | 46 Lb's
| SA28-122C-* ^ |  | 8 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 2.5 Lb's | 57 Lb's
| SA26-70C-* ^ |  | 6 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 1.2 Lb's | 49 Lb's
| SA26-87C-* ^ |  | 6 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 1.8 Lb's | 50 Lb's
ELECTRICAL DATA
|  | Voltage | Phase | Hertz | PSC Mtr | EC Mtr | Total Motor Amps |  | Voltage
[5 empty] | Amps Ea | Amps Ea | PSC | EC | Code
|  | 115 | 1 | 60 | 1 | 0.9 | 2 | 1.8 | A
|  | 208/230 | 1 | 60 | 0.5 | 0.45 | 1 | 0.9 | D
|  | 460 | 1 | 60 | 0.4 | N/A | 0.8 | N/A | F
Notes: | The first * in the listed model numbers designates the unit voltage; A = 115, D = 208/230
The ^ in the listed model numbers designates the unit motor type; P = Perm Split Cap; EC = Electronically Comm
Additional Comments:
SA_SBMTL_0216-A

## SA_2 FAN_EXT
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Super-Flo - Model SA (Rev C)
|  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost Unit Cooler
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2016-02-16 21:08
| CAPACITY (BTUH) @ +25 DEG F SST |  |  |  |  | FAN DATA
| REFRIGERANT R-404A |  |  |  |  | Qty | Fan | CFM | Air Throw | Air Throw
| Unit Model |  | 10 TD | 12 TD |  | Fans | Diameter |  | Std Guard | Hi-Throw
| SA28-106C-* ^ |  | 10600 | 12700 |  | 2 | 12' | 1540 | 15' | 20'
| SA28-134C-* ^ |  | 13400 | 16100 |  | 2 | 12" | 1480 | 15' | 20'
| SA26-115C-* ^ |  | 11500 | 13800 |  | 2 | 12" | 1560 | 15' | 20'
| SA24-84C-* ^ |  | 8400 | 10100 |  | 2 | 12" | 1660 | 15' | 20'
| SA24-105C-* ^ |  | 10500 | 12600 |  | 2 | 12" | 1620 | 15' | 20'
PHYSICAL DATA
| Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net
| Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight
| SA28-106C-* ^ |  | 8 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 2.1 Lb's | 52 Lb's
| SA28-134C-* ^ |  | 8 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 2.7 Lb's | 57 Lb's
| SA26-115C-* ^ |  | 6 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 2.7 Lb's | 56 Lb's
| SA24-84C-* ^ |  | 4 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 2.1 Lb's | 44 Lb's
| SA24-105C-* ^ |  | 4 | 1/2" | 5/8" | 1/4" | 3/4" MPT | 2.7 Lb's | 50 Lb's
ELECTRICAL DATA
|  | Voltage | Phase | Hertz | PSC Mtr | EC Mtr | Total Motor Amps |  | Voltage
[5 empty] | Amps Ea | Amps Ea | PSC | EC | Code
|  | 115 | 1 | 60 | 1 | 0.9 | 2 | 1.8 | A
|  | 208/230 | 1 | 60 | 0.5 | 0.45 | 1 | 0.9 | D
|  | 460 | 1 | 60 | N/A | N/A | 0.54 | N/A | F
Notes: | The first * in the listed model numbers designates the unit voltage; A = 115, D = 208/230
The ^ in the listed model numbers designates the unit motor type; P = Perm Split Cap; EC = Electronically Comm
Additional Comments:
SA_SBMTL_0216-A

## SA_3 FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Super-Flo - Model SA (Rev C)
|  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost Unit Cooler
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2016-02-16 21:08
| CAPACITY (BTUH) @ +25 DEG F SST |  |  |  |  | FAN DATA
| REFRIGERANT R-404A |  |  |  |  | Qty | Fan | CFM | Air Throw | Air Throw
| Unit Model |  | 10 TD | 12 TD |  | Fans | Diameter |  | Std Guard | Hi-Throw
| SA38-160C-* ^ |  | 16000 | 19200 |  | 3 | 12' | 2310 | 15' | 20'
| SA38-195C-* ^ |  | 19500 | 23400 |  | 3 | 12" | 2220 | 15' | 20'
| SA36-145C-* ^ |  | 14500 | 17400 |  | 3 | 12" | 2400 | 15' | 20'
| SA36-170C-* ^ |  | 17000 | 20400 |  | 3 | 12" | 2340 | 15' | 20'
| SA34-130C-* ^ |  | 13000 | 15600 |  | 3 | 12" | 2490 | 15' | 20'
PHYSICAL DATA
| Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net
| Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight
| SA38-160C-* ^ |  | 8 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 3 Lb's | 71 Lb's
| SA38-195C-* ^ |  | 8 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 4 Lb's | 76 Lb's
| SA36-145C-* ^ |  | 6 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 3 Lb's | 70 Lb's
| SA36-170C-* ^ |  | 6 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 4 Lb's | 77 Lb's
| SA34-130C-* ^ |  | 4 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 3 Lb's | 71 Lb's
ELECTRICAL DATA
|  | Voltage | Phase | Hertz | PSC Mtr | EC Mtr | Total Motor Amps |  | Voltage
[5 empty] | Amps Ea | Amps Ea | PSC | EC | Code
|  | 115 | 1 | 60 | 1 | 0.9 | 3 | 2.7 | A
|  | 208/230 | 1 | 60 | 0.5 | 0.45 | 1.5 | 1.35 | D
|  | 460 | 1 | 60 | N/A | N/A | 0.8 | N/A | F
Notes: | The first * in the listed model numbers designates the unit voltage; A = 115, D = 208/230
The ^ in the listed model numbers designates the unit motor type; P = Perm Split Cap; EC = Electronically Comm
Additional Comments:
SA_SBMTL_0216-A

## SA_4 FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Super-Flo - Model SA (Rev C)
|  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost Unit Cooler
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2016-02-16 21:08
| CAPACITY (BTUH) @ +25 DEG F SST |  |  |  |  | FAN DATA
| REFRIGERANT R-404A |  |  |  |  | Qty | Fan | CFM | Air Throw | Air Throw
| Unit Model |  | 10 TD | 12 TD |  | Fans | Diameter |  | Std Guard | Hi-Throw
| SA48-212C-* ^ |  | 21200 | 25400 |  | 4 | 12' | 3080 | 15' | 20'
| SA48-264C-* ^ |  | 26400 | 31700 |  | 4 | 12" | 2960 | 15' | 20'
| SA46-192C-* ^ |  | 19200 | 23000 |  | 4 | 12" | 3200 | 15' | 20'
| SA46-230C-* ^ |  | 23000 | 27600 |  | 4 | 12" | 3120 | 15' | 20'
| SA44-170C-* ^ |  | 17000 | 20400 |  | 4 | 12" | 3320 | 15' | 20'
PHYSICAL DATA
| Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net
| Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight
| SA48-212C-* ^ |  | 8 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 4 Lb's | 127 Lb's
| SA48-264C-* ^ |  | 8 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 5.3 Lb's | 131 Lb's
| SA46-192C-* ^ |  | 6 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 4 Lb's | 127 Lb's
| SA46-230C-* ^ |  | 6 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 5.3 Lb's | 132 Lb's
| SA44-170C-* ^ |  | 4 | 1/2" | 7/8" | 1/4" | 3/4" MPT | 4 Lb's | 126 Lb's
ELECTRICAL DATA
|  | Voltage | Phase | Hertz | PSC Mtr | EC Mtr | Total Motor Amps |  | Voltage
[5 empty] | Amps Ea | Amps Ea | PSC | EC | Code
|  | 115 | 1 | 60 | 1 | 0.9 | 4 | 3.6 | A
|  | 208/230 | 1 | 60 | 0.5 | 0.45 | 2 | 1.8 | D
|  | 460 | 1 | 60 | 0.4 | N/A | 0.8 | N/A | F
Notes: | The first * in the listed model numbers designates the unit voltage; A = 115, D = 208/230
The ^ in the listed model numbers designates the unit motor type; P = Perm Split Cap; EC = Electronically Comm
Additional Comments:
SA_SBMTL_0216-A

## SA_5 FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Super-Flo - Model SA (Rev C)
|  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost Unit Cooler
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2016-02-16 21:08
| CAPACITY (BTUH) @ +25 DEG F SST |  |  |  |  | FAN DATA
| REFRIGERANT R-404A |  |  |  |  | Qty | Fan | CFM | Air Throw | Air Throw
| Unit Model |  | 10 TD | 12 TD |  | Fans | Diameter |  | Std Guard | Hi-Throw
| SA58-275C-* ^ |  | 27500 | 33000 |  | 5 | 12' | 3850 | 15' | 20'
| SA56-245C-* ^ |  | 24500 | 29400 |  | 5 | 12" | 4000 | 15' | 20'
| SA54-215C-* ^ |  | 21500 | 25800 |  | 5 | 12" | 4150 | 15' | 20'
PHYSICAL DATA
| Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net
| Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight
| SA58-275C-* ^ |  | 8 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 4.9 Lb's | 156 Lb's
| SA56-245C-* ^ |  | 6 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 4.9 Lb's | 153 Lb's
| SA54-215C-* ^ |  | 4 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 4.9 Lb's | 150 Lb's
ELECTRICAL DATA
|  | Voltage | Phase | Hertz | PSC Mtr | EC Mtr | Total Motor Amps |  | Voltage
[5 empty] | Amps Ea | Amps Ea | PSC | EC | Code
|  | 115 | 1 | 60 | 1 | 0.9 | 5 | 4.5 | A
|  | 208/230 | 1 | 60 | 0.5 | 0.45 | 2.5 | 2.25 | D
|  | 460 | 1 | 60 | 0.4 | N/A | 2 | N/A | F
Notes: | The first * in the listed model numbers designates the unit voltage; A = 115, D = 208/230
The ^ in the listed model numbers designates the unit motor type; P = Perm Split Cap; EC = Electronically Comm
Additional Comments:
SA_SBMTL_0216-A

## SA_6 FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Super-Flo - Model SA (Rev C)
|  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost Unit Cooler
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2016-02-16 21:08
| CAPACITY (BTUH) @ +25 DEG F SST |  |  |  |  | FAN DATA
| REFRIGERANT R-404A |  |  |  |  | Qty | Fan | CFM | Air Throw | Air Throw
| Unit Model |  | 10 TD | 12 TD |  | Fans | Diameter |  | Std Guard | Hi-Throw
| SA68-318C-* ^ |  | 31800 | 38200 |  | 6 | 12' | 4620 | 15' | 20'
| SA68-390C-* ^ |  | 39000 | 46800 |  | 6 | 12" | 4440 | 15' | 20'
| SA66-295C-* ^ |  | 29500 | 35400 |  | 6 | 12" | 4800 | 15' | 20'
| SA66-345C-* ^ |  | 34500 | 41400 |  | 6 | 12" | 4680 | 15' | 20'
| SA64-255C-* ^ |  | 25500 | 30600 |  | 6 | 12" | 4980 | 15' | 20'
PHYSICAL DATA
| Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net
| Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight
| SA68-318C-* ^ |  | 8 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 5.9 Lb's | 177 Lb's
| SA68-390C-* ^ |  | 8 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 7.8 Lb's | 185 Lb's
| SA66-295C-* ^ |  | 6 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 5.9 Lb's | 177 Lb's
| SA66-345C-* ^ |  | 6 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 7.8 Lb's | 184 Lb's
| SA64-255C-* ^ |  | 4 | 1/2" | 1-1/8" | 1/4" | 3/4" MPT | 5.9 Lb's | 170 Lb's
ELECTRICAL DATA
|  | Voltage | Phase | Hertz | PSC Mtr | EC Mtr | Total Motor Amps |  | Voltage
[5 empty] | Amps Ea | Amps Ea | PSC | EC | Code
|  | 115 | 1 | 60 | 1 | 0.9 | 6 | 5.4 | A
|  | 208/230 | 1 | 60 | 0.5 | 0.45 | 3 | 2.7 | D
|  | 460 | 1 | 60 | 0.4 | N/A | 2 | N/A | F
Notes: | The first * in the listed model numbers designates the unit voltage; A = 115, D = 208/230
The ^ in the listed model numbers designates the unit motor type; P = Perm Split Cap; EC = Electronically Comm
Additional Comments:
SA_SBMTL_0216-A