Job:

Engineer:

Contractor:

Prepared By:

Model:  	     		Date:

EFFICIENT

82% efficiency – highest of any atmospheric boiler available today

THERMAL SHOCK PROOF

Twenty-year warranty against thermal shock damage
up to 150°F differential

Maximum operating temperature: 230°F

LIGHTWEIGHT

A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

Cuts fuel costs substantially because the standby and radiation losses normal to other boilers and tank-type water heaters are eliminated

LOW WATER OPERATING TEMPERATURE

Operates with inlet water temperature as low as 105°F
without condensing

#### Heat Exchanger

ASME Inspected and Stamped
160 PSIG

National Board Listed

Headers

Glass-lined Cast Iron – Standard

Bronze – Option A-1

Finned Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone O-Rings

60 PSIG ASME Pressure Relief Valve

Temperature and Pressure Gauge (Boiler)

Water Connections

Left Hand – Standard

Right Hand – Option A-6

Flow Configuration

Two-pass (Standard)

Single-pass (Cast Iron Only)

#### Controls

120V, 60Hz, 1 Ph Power Supply

120/24V Transformer

100% Pilot Shut-off/Lockout

Electronic, Intermittent Ignition (IID) Pilot

High Limit Control, Manual Reset

High Limit Control, Auto Reset –
Models 3001-4001

On/Off Switch

Flow Switch

Economaster Pump Time Delay

#### Gas Control Train

Manual Main Gas Shut-off Cock

Main Gas Pressure Regulator

Redundant Safety Shut-off Valve

Control Valve

Firing Mode

On/off (H4)

Two-stage Firing (H3)

Four-stage Firing (H9)

Motorized Modulation (H2)

Fuel

Natural Gas

Propane Gas

Design Certified ANSI Z21.13/
CSA 4.9

#### Construction

CSA Low Lead Certified ≤ .25% Lead

Front Controls

Stainless Steel Burners

Polytuf Powder Coat Finish

Built-in Draft Diverter

Draft Inducer

Motorized Draft Inducer – 
Option D-2

#### Temperature Controllers

B-6	Two-Stage (H3)

B-35	4-20 mA (H2)

B-  	TempTracker Mod+ Hybrid, 2-16 Boilers (All)

B-40	Motorized Modulation (H2)

B-41	Motorized Modulation, Outdoor reset (H2)

B-  	Two-stage Digital (H3)

B-  	Four-stage Digital (H9)

B-60	Stage Interface (H3/H9)

#### Additional Safety Controls

F-9	Low Water Cut-off Probe

I-1	High Limit Control, 
Auto Reset

S-1	Low Gas Pressure Switch

S-2	High Gas Pressure Switch

#### Regulatory Agency Requirements

Raytherm - Type H

Hydronic Heating Boilers	Model

# Text boxes

# Raytherm® - Type H

## Hydronic Heating Boilers
Commercial

Models 2100-4001 (Indoor)

Proudly Assembled in the USA

MODELS H 2100 THRU 4001

| Model No. | MBTUH Natural and Propane Gas | Dimensions (inches) | Electrical Rating | Approx. Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- |
|  |  | Width | Overall Height | Gas Conn. | Water Conn. | Flue Dia |  |  |
|  | Input | Output | A | B | G | H | K |  |  |
| H-2100 | 2100 | 1722 | 61.0 | 68-1/4 | * | 3** | 24 | Less than 8.0 amps without pump at 120VAC | 1400 |
| H-2500 | 2499 | 2049 | 70.0 | 68-1/4 | * | 3** | 26 |  | 1580 |
| H-3001 | 3000 | 2460 | 81-1/4 | 68-1/4 | 2 | 3** | 28 |  | 1750 |
| H-3500 | 3500 | 2870 | 92-1/2 | 68-1/4 | 2 | 3** | 30 |  | 1920 |
| H-4001 | 4000 | 3280 | 103-3/4 | 68-1/4 | 2 | 3** | 32 |  | 2100 |
| NOTE: Ratings are for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings 4% for every 1,000 feet above sea level | * 1-1/2” or 2” contingent on boiler type code requirements ** 4” on one-pass option |

BOILER RATE OF FLOW AND PRESSURE DROP

|  | Model No. | 10º ΔT | 20º ΔT | 30º ΔT | 40º ΔT | Minimum Flow | Maximum Flow |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | GPM | ΔP FT | GPM | ΔP FT | GPM | ΔP FT | GPM | ΔP FT | GPM | ΔP FT | ΔT | GPM | ΔP FT | ΔT |
| TWO-PASS | H-2100 |  | 174 | 11.2 | 116 | 5.1 |  |  | 90 | 3.2 | 38 | 200 | 14.8 | 17 |
|  | H-2500 | Exceeds Maximum Flow | 138 | 7.8 | 103 | 4.4 | 103 | 4.4 | 40 | 200 | 15.8 | 21 |
|  | H-3001 |  | 166 | 11.6 | 124 | 6.7 | 124 | 6.7 | 40 | 200 | 16.7 | 25 |
|  | H-3500 |  | 191 | 16.2 | 145 | 9.5 | 145 | 9.5 | 40 | 200 | 17.5 | 29 |
|  | H-4001 |  |  | 166 | 13.0 | 166 | 13.0 | 40 | 200 | 18.7 | 33 |
| ONE-PASS | H-2100 | 344 | 14.0 |  | Less than Minimum Flow | 180 | 4.0 | 19 | 400 | 18.0 | 9 |
|  | H-2500 | 400 | 18.8 | 205 | 5.3 |  | 180 | 4.1 | 23 | 400 | 18.8 | 10 |
|  | H-3001 |  | 246 | 7.8 |  | 180 | 4.3 | 27 | 400 | 19.5 | 12 |
|  | H-3500 |  | 287 | 11.0 | 191 | 5.0 |  | 180 | 4.5 | 32 | 400 | 20.5 | 14 |
|  | H-4001 |  | 328 | 14.8 | 219 | 6.8 |  | 180 | 4.7 | 36 | 400 | 21.5 | 16 |

NOTES:

- Values represent maximum flows and pressure drops for closed heating systems

- Maximum acceptable flow through heat exchanger tubes is 200 GPM (two pass); 400 GPM (one-pass)

- Single-pass heat exchangers are to be used only when flow rates exceed the allowable for two-pass

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com