## SUB_INDEX
|  | HEAT TRANSFER PRODUCTS GROUP, LLC |  | SUBMITTAL DATA INDEX
|  | 3885 Crestwood Parkway / Suite 500 |  | Model Series - KDS / KDD
|  | Duluth, GA 30096 |  | QUANTUM AIR
(P) 800-288-9488 / (F) 256-259-7478
|  | http://kramer.htpgusa.com |  | Remote - Air Cooled Condenser
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
SUBMITTAL DATA INDEX
1-1/2 HP / 850 RPM MODELS
|  | SINGLE WIDE MODELS | DOUBLE WIDE MODELS
|  | KDS004*D1A | KDD019*D2A
|  | KDS005*D1A | KDD028*D2A
|  | KDS007*D1A | KDD031*D2A
|  | KDS010*D2A | KDD041*D3A
|  | KDS014*D2A | KDD048*D3A
|  | KDS015*D2A | KDD055*D4A
|  | KDS021*D3A | KDD065*D4A
|  | KDS024*D3A | KDD069*D5A
|  | KDS028*D4A | KDD086*D5A
|  | KDS032*D4A | KDD103*D6A
|  | KDS035*D5A | KDD121*D7A
KDS043*D5A
KDS052*D6A
KDS060*D7A
MODEL NUMBER KEY
K D S 004 E D 1 A
A = Revison Code
K = Kramer
# Fans Long
1 thru 7
| D = Condenser |  |  | Motor RPM / HP
B = 1140 / 1.5 HP
D = 850 / 1.5 HP
| S = Single Wide |  |  | L = 850 / 1 HP
| D = Double Wide |  |  | E = 550 / 1/3 HP
Voltage Code
| Capacity = MBH / THR |  |  | E = 208/230/3/60
| Per Degree TD / 10 FPI |  |  | G = 460/3/60
J = 575/3/60
N = 200/220/3/50
Q = 380/3/50
X = Other
KDS_KDD_INDEX_1116_NEW

## KDS004_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 3.7 | 4 | 4.3 | 4.7
|  |  | R-407A ^ | 3.3 | 3.6 | 3.8 | 4
|  |  | R-448A ^ | 3.3 | 3.6 | 3.8 | 4
|  |  | R-449A ^ | 3.3 | 3.6 | 3.8 | 4
|  |  | R-407C ^ | 3.2 | 3.5 | 3.7 | 3.9
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1-1/2 | 850 | 8600 | 1-1/8" | 7/8" | 62.2 | 4.5 Lb's | 16.7 Lb's | 350 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.5 | 6.5 | 15 | 15
|  |  | 460 | 3 | 1.5 | 3.3 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS005_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 5.1 | 5.6 | 5.9 | 6.5
|  |  | R-407A ^ | 4.7 | 5.2 | 5.4 | 5.7
|  |  | R-448A ^ | 4.7 | 5.2 | 5.4 | 5.7
|  |  | R-449A ^ | 4.7 | 5.2 | 5.4 | 5.7
|  |  | R-407C ^ | 4.6 | 5.1 | 5.3 | 5.6
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1-1/2 | 850 | 8400 | 1-1/8" | 7/8" | 62.2 | 6.6 Lb's | 25 Lb's | 375 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.5 | 6.5 | 15 | 15
|  |  | 460 | 3 | 1.5 | 3.3 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS007_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 6.3 | 6.9 | 7.3 | 8
|  |  | R-407A ^ | 5.9 | 6.5 | 6.8 | 7.1
|  |  | R-448A ^ | 5.9 | 6.5 | 6.8 | 7.1
|  |  | R-449A ^ | 5.9 | 6.5 | 6.8 | 7.1
|  |  | R-407C ^ | 5.8 | 6.4 | 6.7 | 7
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1-1/2 | 850 | 8210 | 1-1/8" | 7/8" | 62.2 | 8.8 Lb's | 32.6 Lb's | 400 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.5 | 6.5 | 15 | 15
|  |  | 460 | 3 | 1.5 | 3.3 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS010_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 9.5 | 10.4 | 11 | 12.1
|  |  | R-407A ^ | 9 | 9.9 | 10.5 | 10.9
|  |  | R-448A ^ | 9 | 9.9 | 10.5 | 10.9
|  |  | R-449A ^ | 9 | 9.9 | 10.5 | 10.9
|  |  | R-407C ^ | 8.8 | 9.7 | 10.3 | 10.7
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1-1/2 | 850 | 17200 | 1-3/8" | 1-1/8" | 65.2 | 8.8 Lb's | 33.2 Lb's | 725 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.9 | 13 | 15 | 20
|  |  | 460 | 3 | 2.9 | 6.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS014_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 12.8 | 14 | 14.8 | 16.3
|  |  | R-407A ^ | 12.6 | 13.8 | 14.6 | 15.2
|  |  | R-448A ^ | 12.6 | 13.8 | 14.6 | 15.2
|  |  | R-449A ^ | 12.6 | 13.8 | 14.6 | 15.2
|  |  | R-407C ^ | 12.4 | 13.5 | 14.3 | 14.9
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1-1/2 | 850 | 16800 | 1-3/8" | 1-1/8" | 65.2 | 13.3 Lb's | 50.1 Lb's | 750 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.9 | 13 | 15 | 20
|  |  | 460 | 3 | 2.9 | 6.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS015_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 14.3 | 15.7 | 16.5 | 18.2
|  |  | R-407A ^ | 13.9 | 15.3 | 16.1 | 16.8
|  |  | R-448A ^ | 13.9 | 15.3 | 16.1 | 16.8
|  |  | R-449A ^ | 13.9 | 15.3 | 16.1 | 16.8
|  |  | R-407C ^ | 13.6 | 15 | 15.8 | 16.5
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1-1/2 | 850 | 16420 | 1-3/8" | 1-1/8" | 65.2 | 17.7 Lb's | 65.3 Lb's | 775 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.9 | 13 | 15 | 20
|  |  | 460 | 3 | 2.9 | 6.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS021_3FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 19.3 | 21.2 | 22.4 | 24.6
|  |  | R-407A ^ | 19.1 | 20.9 | 22.1 | 23
|  |  | R-448A ^ | 19.1 | 20.9 | 22.1 | 23
|  |  | R-449A ^ | 19.1 | 20.9 | 22.1 | 23
|  |  | R-407C ^ | 18.7 | 20.5 | 21.7 | 22.6
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
3 | 30" | 1-1/2 | 850 | 25200 | 1-5/8" | 1-3/8" | 67 | 19.9 Lb's | 75.2 Lb's | 1,125 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.4 | 19.5 | 21.1 | 25
|  |  | 460 | 3 | 4.4 | 9.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS024_3FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 21.9 | 24 | 25.4 | 27.9
|  |  | R-407A ^ | 22.3 | 24.4 | 25.8 | 26.9
|  |  | R-448A ^ | 22.3 | 24.4 | 25.8 | 26.9
|  |  | R-449A ^ | 22.3 | 24.4 | 25.8 | 26.9
|  |  | R-407C ^ | 21.9 | 23.9 | 25.3 | 26.4
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
3 | 30" | 1-1/2 | 850 | 24630 | 1-5/8" | 1-3/8" | 67 | 26.5 Lb's | 97.9 Lb's | 1,150 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.4 | 19.5 | 21.1 | 25
|  |  | 460 | 3 | 4.4 | 9.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS028_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 25.7 | 28.2 | 29.8 | 32.7
|  |  | R-407A ^ | 25.2 | 27.7 | 29.2 | 30.4
|  |  | R-448A ^ | 25.2 | 27.7 | 29.2 | 30.4
|  |  | R-449A ^ | 25.2 | 27.7 | 29.2 | 30.4
|  |  | R-407C ^ | 24.7 | 27.2 | 28.6 | 29.8
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 850 | 33600 | 1-5/8" | 1-3/8" | 68.2 | 26.6 Lb's | 100.3 Lb's | 1,500 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 5.8 | 26 | 30.1 | 35
|  |  | 460 | 3 | 5.8 | 13.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS032_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 28.9 | 31.7 | 33.5 | 26.8
|  |  | R-407A ^ | 29.4 | 32.2 | 34 | 35.4
|  |  | R-448A ^ | 29.4 | 32.2 | 34 | 35.4
|  |  | R-449A ^ | 29.4 | 32.2 | 34 | 35.4
|  |  | R-407C ^ | 28.8 | 31.6 | 33.3 | 34.7
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 850 | 32840 | 1-5/8" | 1-3/8" | 68.2 | 35.3 Lb's | 130.6 Lb's | 1,525 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 5.8 | 26 | 30.1 | 35
|  |  | 460 | 3 | 5.8 | 13.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS035_5FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 31.4 | 34.4 | 36.4 | 40
R-407A ^ | 31.5 | 34.5 | 36.5 | 38
R-448A ^ | 31.5 | 34.5 | 36.5 | 38
R-449A ^ | 31.5 | 34.5 | 36.5 | 38
R-407C ^ | 30.9 | 33.8 | 35.8 | 37.3 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
5 | 30" | 1-1/2 | 850 | 42000 | 2-1/8" | 1-5/8" | 69.2 | 55.5 Lb's | 216.2 Lb's | 1,875 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.3 | 32.5 | 34.1 | 40
|  |  | 460 | 3 | 7.3 | 16.5 | 17.3 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS043_5FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 37.9 | 41.5 | 43.8 | 48.2
R-407A ^ | 39.3 | 43.1 | 45.5 | 47.4
R-448A ^ | 39.3 | 43.1 | 45.5 | 47.4
R-449A ^ | 39.3 | 43.1 | 45.5 | 47.4
R-407C ^ | 38.5 | 42.2 | 44.6 | 46.5 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
5 | 30" | 1-1/2 | 850 | 41050 | 2-1/8" | 1-5/8" | 69.2 | 75.9 Lb's | 282 Lb's | 1,900 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.3 | 32.5 | 34.1 | 40
|  |  | 460 | 3 | 7.3 | 16.5 | 17.3 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS052_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 45.4 | 49.8 | 52.6 | 57.8
R-407A ^ | 47.2 | 51.7 | 54.6 | 56.9
R-448A ^ | 47.2 | 51.7 | 54.6 | 56.9
R-449A ^ | 47.2 | 51.7 | 54.6 | 56.9
R-407C ^ | 46.3 | 50.7 | 53.5 | 55.8 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1-1/2 | 850 | 49260 | 2-1/8" | 1-5/8" | 70 | 91 Lb's | 338.3 Lb's | 2,275 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 8.7 | 39 | 40.6 | 45
|  |  | 460 | 3 | 8.7 | 19.8 | 20.6 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDS060_7FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 53.1 | 58.2 | 61.4 | 67.6
R-407A ^ | 55 | 60.3 | 63.7 | 66.3
R-448A ^ | 55 | 60.3 | 63.7 | 66.3
R-449A ^ | 55 | 60.3 | 63.7 | 66.3
R-407C ^ | 53.9 | 59.1 | 62.4 | 65 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
7 | 30" | 1-1/2 | 850 | 57470 | 2-1/8" | 1-5/8" | 70.6 | 106.2 Lb's | 304.7 Lb's | 2,650 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 10.2 | 45.5 | 47.1 | 50
|  |  | 460 | 3 | 10.2 | 23.1 | 25.1 | 30
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD019_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 18.4 | 20.2 | 21.3 | 23.5
|  |  | R-407A ^ | 17.5 | 19.2 | 20.3 | 21.1
|  |  | R-448A ^ | 17.5 | 19.2 | 20.3 | 21.1
|  |  | R-449A ^ | 17.5 | 19.2 | 20.3 | 21.1
|  |  | R-407C ^ | 17.2 | 18.8 | 19.9 | 20.7
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 850 | 34400 | 1-3/8" | 1-1/8" | 68.2 | 17.7 Lb's | 166.8 Lb's | 1,500 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 5.8 | 26 | 30.1 | 35
|  |  | 460 | 3 | 5.8 | 13.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD028_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://www.kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 25.6 | 28.1 | 29.7 | 32.6
|  |  | R-407A ^ | 25.2 | 27.7 | 29.2 | 30.4
|  |  | R-448A ^ | 25.2 | 27.7 | 29.2 | 30.4
|  |  | R-449A ^ | 25.2 | 27.7 | 29.2 | 30.4
|  |  | R-407C ^ | 24.7 | 27.2 | 28.6 | 29.8
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 850 | 33600 | 1-3/8" | 1-1/8" | 68.2 | 26.6 Lb's | 100.3 Lb's | 1,525 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 5.8 | 26 | 30.1 | 35
|  |  | 460 | 3 | 5.8 | 13.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD031_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 28.1 | 30.8 | 32.5 | 35.8
|  |  | R-407A ^ | 28.6 | 31.3 | 33.1 | 34.4
|  |  | R-448A ^ | 28.6 | 31.3 | 33.1 | 34.4
|  |  | R-449A ^ | 28.6 | 31.3 | 33.1 | 34.4
|  |  | R-407C ^ | 28 | 30.7 | 32.4 | 33.7
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 850 | 32840 | 1-3/8" | 1-1/8" | 68.2 | 35.3 Lb's | 355.3 Lb's | 1,550 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 5.8 | 26 | 30.1 | 35
|  |  | 460 | 3 | 5.8 | 13.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD041_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 38 | 41.7 | 44 | 48.5
|  |  | R-407A ^ | 37.5 | 41.1 | 43.4 | 45.2
|  |  | R-448A ^ | 37.5 | 41.1 | 43.4 | 45.2
|  |  | R-449A ^ | 37.5 | 41.1 | 43.4 | 45.2
|  |  | R-407C ^ | 36.8 | 40.3 | 42.5 | 44.3
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1-1/2 | 850 | 50400 | 1-5/8" | 1-3/8" | 70 | 39.9 Lb's | 228 Lb's | 2,275 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 8.7 | 39 | 40.6 | 45
|  |  | 460 | 3 | 8.7 | 19.8 | 20.6 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD048_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 43.4 | 47.6 | 50.2 | 55.3
|  |  | R-407A ^ | 44.1 | 48.4 | 51.1 | 53.2
|  |  | R-448A ^ | 44.1 | 48.4 | 51.1 | 53.2
|  |  | R-449A ^ | 44.1 | 48.4 | 51.1 | 53.2
|  |  | R-407C ^ | 43.2 | 47.4 | 50.1 | 52.1
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1-1/2 | 850 | 49260 | 1-5/8" | 1-3/8" | 70 | 53 Lb's | 195.8 Lb's | 2,300 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 8.7 | 39 | 40.6 | 45
|  |  | 460 | 3 | 8.7 | 19.8 | 20.6 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD055_8FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW |  |  |  |  | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 51.4 | 56.4 | 59.5 | 65.5
|  |  | R-407A ^ | 50.6 | 55.4 | 58.6 | 61
|  |  | R-448A ^ | 51.4 | 56.4 | 59.5 | 65.5
|  |  | R-449A ^ | 50.6 | 55.4 | 58.6 | 61
|  |  | R-407C ^ | 49.6 | 54.3 | 57.4 | 59.8
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
8 | 30" | 1-1/2 | 850 | 67200 | 1-5/8" | 1-3/8" | 71.2 | 53.2 Lb's | 200.6 Lb's | 3,025 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 11.6 | 52 | 53.6 | 60
|  |  | 460 | 3 | 11.6 | 26.4 | 27.2 | 30
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD065_8FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW |  |  |  |  | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 57.8 | 63.4 | 67 | 73.7
|  |  | R-407A ^ | 58.9 | 64.5 | 68.2 | 71
|  |  | R-448A ^ | 58.9 | 64.5 | 68.2 | 71
|  |  | R-449A ^ | 58.9 | 64.5 | 68.2 | 71
|  |  | R-407C ^ | 57.7 | 63.2 | 66.8 | 69.6
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
8 | 30" | 1-1/2 | 850 | 65680 | 1-5/8" | 1-3/8" | 71.2 | 70.6 Lb's | 261 Lb's | 3,050 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 11.6 | 52 | 53.6 | 60
|  |  | 460 | 3 | 11.6 | 26.4 | 27.2 | 30
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD069_10FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 62.9 | 69 | 72.8 | 8.01
R-407A ^ | 63 | 69.1 | 73 | 76
R-448A ^ | 63 | 69.1 | 73 | 76
R-449A ^ | 63 | 69.1 | 73 | 76
R-407C ^ | 61.8 | 67.7 | 71.6 | 74.5 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
10 | 30" | 1-1/2 | 850 | 84000 | 2-1/8" | 1-5/8" | 72.2 | 110.9 Lb's | 432.2 Lb's | 3,775 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 14.5 | 65 | 66.6 | 70
|  |  | 460 | 3 | 14.5 | 33 | 35.1 | 40
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD086_10FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 75.8 | 83.1 | 87.8 | 96.6
R-407A ^ | 78.6 | 86.2 | 91 | 94.8
R-448A ^ | 78.6 | 86.2 | 91 | 94.8
R-449A ^ | 78.6 | 86.2 | 91 | 94.8
R-407C ^ | 77 | 84.5 | 89.2 | 92.9 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
10 | 30" | 1-1/2 | 850 | 82100 | 2-1/8" | 1-5/8" | 72.2 | 151.7 Lb's | 563.9 Lb's | 3,800 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 14.5 | 65 | 66.6 | 70
|  |  | 460 | 3 | 14.5 | 33 | 35.1 | 40
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD103_12FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 90.9 | 99.7 | 105.3 | 115.8
R-407A ^ | 94.2 | 103.3 | 109.1 | 113.7
R-448A ^ | 94.2 | 103.3 | 109.1 | 113.7
R-449A ^ | 94.2 | 103.3 | 109.1 | 113.7
R-407C ^ | 92.3 | 101.2 | 106.9 | 111.4 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
12 | 30" | 1-1/2 | 850 | 98520 | 2-1/8" | 1-5/8" | 73 | 182 Lb's | 676.6 Lb's | 4,550 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 17.4 | 78 | 80.1 | 90
|  |  | 460 | 3 | 17.4 | 39.6 | 40.4 | 45
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## KDD121_14FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - KDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://kramer.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 106 | 116.3 | 122.8 | 135
R-407A ^ | 110 | 120.6 | 127.3 | 132.7
R-448A ^ | 110 | 120.6 | 127.3 | 132.7
R-449A ^ | 110 | 120.6 | 127.3 | 132.7
R-407C ^ | 107.8 | 118.2 | 124.8 | 130.1 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) # | (Winter) # | Weight
14 | 30" | 1-1/2 | 850 | 114940 | 2-1/8" | 1-5/8" | 72 | 212.3 Lb's | 789.5 Lb's | 5,300 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 20.3 | 91 | 92.6 | 100
|  |  | 460 | 3 | 20.3 | 46.2 | 47 | 50
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A