Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:

EFFICIENT

82% thermal efficiency – highest of any atmospheric
boiler available today

THERMAL SHOCK PROOF

Twenty-year warranty against thermal shock damage
up to 150°F differential

Maximum operating temperature: 230°F

LIGHTWEIGHT

A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

Cuts fuel costs substantially because the standby and radiation losses normal to other boilers are eliminated

LOW WATER OPERATING TEMPERATURE

Operates with inlet water temperature as low as 105°F
without condensing

#### Heat Exchanger

ASME Inspected and Stamped
160 PSIG

National Board Listed

Headers

Glass-lined Cast Iron – Standard

Bronze – Option A-1

Finned Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone O-Rings

60 PSIG ASME Pressure Relief Valve

Temperature and Pressure Gauge

Water Connections

Left Hand – Standard

Right Hand – Option A-6

Pump, Rear-mounted – Optional

4.25” Impeller

4.7” Impeller

#### Controls

120V, 60Hz, 1 Ph Power Supply

120/24V Transformer

100% Pilot Shut-off/Lockout

Electronic, Intermittent Ignition (IID) Pilot

High Limit Control, Manual Reset

On/Off Switch

Flow Switch

Economaster Pump Time Delay

#### Gas Train

Manual Main Gas Shut-off Cock

Main Gas Pressure Regulator

Redundant Safety Shut-off Valve

Control Valve

Firing Mode

On/off (H4)

Two-stage Firing (H3)

Four-stage Firing (H9)

Mechanical Modulation,
110-170°F (H5)

Mechanical Modulation, 
150-210°F (H1)

Motorized Modulation (H2)

Fuel

Natural Gas

Propane Gas

Design Certified ANSI Z21.13/CSA 4.9

#### Construction

CSA Low Lead Certified ≤ .25% Lead

Front Controls

Stainless Steel Burners

Polytuf Powder Coat Finish

Vent Selection

Draft Diverter (Indoor) – Option D-10

Power Vent, Loose (Indoor) – 
Option D-2

Stackless Top (Outdoor) – 
Option D-11

Base (Optional)

Combustible Floor Shield

#### Temperature Controllers

Note:  H1 and H5 require a system controller

B-6	Two-stage-Mechanical

B-40	Motorized Modulation

B-41	Motorized Modulation, outdoor reset

B-   	Two-stage Digital

B-   	Four-stage Digital

B-35	4-20 mA

B-60	Stage Interface

B-   	TempTracker Mod+ Hybrid 2-16 Boilers

#### Additional Safety Controls

F-9	Low Water Cut-off Probe

I-1	High Limit Control, Auto Reset

S-1	Low Gas Pressure Switch

S-2	High Gas Pressure Switch

#### Regulatory Agency Requirements

Raytherm - Type H

Hydronic Heating Boilers	Model

# Text boxes

# Raytherm® - Type H

## Hydronic Heating Boilers
Commercial

Models 514-824

Proudly Assembled in the USA

.

.

| Model No. | 10º ΔT | 20º ΔT | 30º ΔT | Minimum Flow | Maximum Flow |
| --- | --- | --- | --- | --- | --- |
|  | GPM | ΔP FT | GPM | ΔP FT | GPM | ΔP FT | GPM | ΔP (ft) | ΔT | GPM | ΔP (ft) | ΔT |
| H-514 | 84 | 7.8 | 42 | 1.9 | N/A | N/A | 40 | 1.8 | 21 | 90 | 9 | 9 |
| H-624 | N/A | N/A | 52 | 3.0 | N\A | N\A | 40 | 1.9 | 26 | 90 | 9.5 | 12 |
| H-724 | N/A | N/A | 60 | 4.4 | 40 | 2.0 | 40 | 2.0 | 30 | 90 | 10 | 13 |
| H-824 | N/A | N/A | 68 | 6.0 | 46 | 2.8 | 40 | 2.1 | 34 | 90 | 10.5 | 15 |

N/A – Not Applicable

MODELS H 514-824

|  | Indoor and Outdoor | Dimensions (Inches) | Electrical Rating | Approx. Shipping Weight (Lbs.) |
| --- | --- | --- | --- | --- |
| Model Number | MBTU Input (a) | MBTU Output (a) | Width A | Flue Dia. K | L | With Pump | Without Pump |  |
| H-514 | 511.5 | 419.4 | 32-3/4 | 10 | 25-3/8 | Less than 10 amps @ 120 V | Less than 4 amps @ 120V | 455 |
| H-624 | 627.0 | 514.0 | 37-1/2 | 12 | 29-1/2 |  |  | 465 |
| H-724 | 726.0 | 595.0 | 41-5/8 | 12 | 34-1/4 |  |  | 575 |
| H-824 | 825.0 | 676.5 | 45-3/4 | 14 | 38-1/2 |  |  | 605 |

Note: 	Ratings shown are for elevations up to 2,000 feet. For elevations over 2,000 feet, reduce ratings

at the rate of 4% for each 1,000 feet above sea level.

(a) Propane Input/Output is 94% of stated value.

BOILER RATE OF FLOW AND PRESSURE DROP

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com