## SUB_INDEX
|  | HEAT TRANSFER PRODUCTS GROUP, LLC |  | SUBMITTAL DATA INDEX
|  | 3885 Crestwood Parkway / Suite 500 |  | Model Series - RDS / RDD
|  | Duluth, GA 30096 |  | QUANTUM AIR
(P) 800-288-9488 / (F) 256-259-7478
|  | http://russell.htpgusa.com |  | Remote - Air Cooled Condenser
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
SUBMITTAL DATA INDEX
1-1/2 HP / 1140 RPM MODELS
|  | SINGLE WIDE MODELS | DOUBLE WIDE MODELS
|  | RDS004*B1A | RDD022*B2A
|  | RDS006*B1A | RDD030*B2A
|  | RDS007*B1A | RDD036*B2A
|  | RDS012*B2A | RDD045*B3A
|  | RDS015*B2A | RDD054*B3A
|  | RDS018*B2A | RDD059*B4A
|  | RDS022*B3A | RDD072*B4A
|  | RDS027*B3A | RDD078*B5A
|  | RDS030*B4A | RDD094*B5A
|  | RDS036*B4A | RDD113*B6A
|  | RDS039*B5A | RDD131*B7A
RDS047*B5A
RDS056*B6A
RDS065*B7A
MODEL NUMBER KEY
R D S 004 E B 1 A
A = Revison Code
R = Russell
# Fans Long
1 thru 7
| D = Condenser |  |  | Motor RPM / HP
B = 1140 / 1.5 HP
D = 850 / 1.5 HP
| S = Single Wide |  |  | L = 850 / 1 HP
| D = Double Wide |  |  | E = 550 / 1/3 HP
Voltage Code
| Capacity = MBH / THR |  |  | E = 208/230/3/60
| Per Degree TD / 10 FPI |  |  | G = 460/3/60
J = 575/3/60
N = 200/220/3/50
Q = 380/3/50
X = Other
RDS_RDD_INDEX_1116_NEW

## RDS004_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 4.2 | 4.6 | 4.9 | 5.1
|  |  | R-407A ^ | 4 | 4.4 | 4.9 | 5.1
|  |  | R-448A ^ | 4 | 4.4 | 4.9 | 5.1
|  |  | R-449A ^ | 4 | 4.4 | 4.9 | 5.1
|  |  | R-407C ^ | 3.9 | 4.3 | 4.8 | 5
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1-1/2 | 1140 | 10200 | 1-1/8" | 7/8" | 69.8 | 4.5 Lb's | 16.7 Lb's | 350 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.8 | 6.5 | 15 | 15
|  |  | 460 | 3 | 1.8 | 3.3 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS006_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 5.6 | 6.2 | 6.5 | 6.8
|  |  | R-407A ^ | 5.5 | 6.1 | 6.4 | 6.7
|  |  | R-448A ^ | 5.5 | 6.1 | 6.4 | 6.7
|  |  | R-449A ^ | 5.5 | 6.1 | 6.4 | 6.7
|  |  | R-407C ^ | 5.4 | 6 | 6.3 | 6.6
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1-1/2 | 1140 | 10000 | 1-1/8" | 7/8" | 69.8 | 6.6 Lb's | 25 Lb's | 375 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.8 | 6.5 | 15 | 15
|  |  | 460 | 3 | 1.8 | 3.3 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS007_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 4.2 | 4.6 | 4.9 | 5.1
|  |  | R-407A ^ | 6.8 | 7.4 | 7.8 | 8.2
|  |  | R-448A ^ | 6.8 | 7.4 | 7.8 | 8.2
|  |  | R-449A ^ | 6.8 | 7.4 | 7.8 | 8.2
|  |  | R-407C ^ | 6.7 | 7.3 | 7.7 | 8
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1-1/2 | 1140 | 9800 | 1-1/8" | 7/8" | 69.8 | 8.8 Lb's | 32.6 Lb's | 400 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.8 | 6.5 | 15 | 15
|  |  | 460 | 3 | 1.8 | 3.3 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS012_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 11.2 | 12.3 | 12.9 | 13.6
|  |  | R-407A ^ | 10.9 | 11.9 | 12.6 | 13.2
|  |  | R-448A ^ | 10.9 | 11.9 | 12.6 | 13.2
|  |  | R-449A ^ | 10.9 | 11.9 | 12.6 | 13.2
|  |  | R-407C ^ | 10.7 | 11.7 | 12.4 | 13
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1-1/2 | 1140 | 20400 | 1-3/8" | 1-1/8" | 72.8 | 8.8 Lb's | 33.2 Lb's | 725 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 3.6 | 13 | 15 | 20
|  |  | 460 | 3 | 3.6 | 6.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS015_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 14 | 15.3 | 16.2 | 17
|  |  | R-407A ^ | 13.6 | 14.9 | 15.8 | 16.5
|  |  | R-448A ^ | 13.6 | 14.9 | 15.8 | 16.5
|  |  | R-449A ^ | 13.6 | 14.9 | 15.8 | 16.5
|  |  | R-407C ^ | 13.3 | 14.6 | 15.5 | 16.2
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1-1/2 | 1140 | 20000 | 1-3/8" | 1-1/8" | 72.8 | 13.3 Lb's | 50.1 Lb's | 750 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 3.6 | 13 | 15 | 20
|  |  | 460 | 3 | 3.6 | 6.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS018_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 16.6 | 18.2 | 19.3 | 20.2
|  |  | R-407A ^ | 16.7 | 18.3 | 19.4 | 20.3
|  |  | R-448A ^ | 16.7 | 18.3 | 19.4 | 20.3
|  |  | R-449A ^ | 16.7 | 18.3 | 19.4 | 20.3
|  |  | R-407C ^ | 16.4 | 18 | 19 | 19.9
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1-1/2 | 1140 | 19600 | 1-3/8" | 1-1/8" | 72.8 | 17.7 Lb's | 65.3 Lb's | 775 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 3.6 | 13 | 15 | 20
|  |  | 460 | 3 | 3.6 | 6.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS022_3FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 20.9 | 23 | 24.3 | 25.4
|  |  | R-407A ^ | 20.5 | 22.5 | 23.7 | 24.9
|  |  | R-448A ^ | 20.5 | 22.5 | 23.7 | 24.9
|  |  | R-449A ^ | 20.5 | 22.5 | 23.7 | 24.9
|  |  | R-407C ^ | 20.1 | 22.1 | 23.2 | 24.4
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
3 | 30" | 1-1/2 | 1140 | 30000 | 1-5/8" | 1-3/8" | 74.6 | 19.9 Lb's | 75.2 Lb's | 1,125 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 5.4 | 19.5 | 21.1 | 25
|  |  | 460 | 3 | 5.4 | 9.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS027_3FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 24.4 | 26.8 | 28.3 | 29.7
|  |  | R-407A ^ | 24.7 | 27.1 | 28.6 | 30
|  |  | R-448A ^ | 24.7 | 27.1 | 28.6 | 30
|  |  | R-449A ^ | 24.7 | 27.1 | 28.6 | 30
|  |  | R-407C ^ | 24.2 | 26.6 | 28 | 29.4
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
3 | 30" | 1-1/2 | 1140 | 29400 | 1-5/8" | 1-3/8" | 74.6 | 26.5 Lb's | 97.9 Lb's | 1,150 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 5.4 | 19.5 | 21.1 | 25
|  |  | 460 | 3 | 5.4 | 9.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS030_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 27.9 | 30.6 | 32.3 | 33.9
|  |  | R-407A ^ | 27.3 | 30 | 31.7 | 33.2
|  |  | R-448A ^ | 27.3 | 30 | 31.7 | 33.2
|  |  | R-449A ^ | 27.3 | 30 | 31.7 | 33.2
|  |  | R-407C ^ | 26.8 | 29.4 | 31.1 | 32.5
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 1140 | 40000 | 1-5/8" | 1-3/8" | 75.8 | 26.6 Lb's | 100.3 Lb's | 1,500 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.2 | 26 | 30.1 | 35
|  |  | 460 | 3 | 7.2 | 13.2 | 15.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS036_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 32.4 | 35.5 | 37.5 | 39.4
|  |  | R-407A ^ | 32.7 | 35.8 | 37.9 | 39.7
|  |  | R-448A ^ | 32.7 | 35.8 | 37.9 | 39.7
|  |  | R-449A ^ | 32.7 | 35.8 | 37.9 | 39.7
|  |  | R-407C ^ | 32.1 | 35.1 | 37.1 | 38.2
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 1140 | 39200 | 1-5/8" | 1-3/8" | 75.8 | 35.3 Lb's | 130.6 Lb's | 1,525 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.2 | 26 | 30.1 | 35
|  |  | 460 | 3 | 7.2 | 13.2 | 15.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS039_5FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 35.7 | 39.1 | 41.3 | 43.4
R-407A ^ | 35.6 | 39 | 41.2 | 43.3
R-448A ^ | 35.6 | 39 | 41.2 | 43.3
R-449A ^ | 35.6 | 39 | 41.2 | 43.3
R-407C ^ | 34.9 | 38.2 | 40.4 | 42.4 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
5 | 30" | 1-1/2 | 1140 | 50000 | 2-1/8" | 1-5/8" | 76.8 | 55.5 Lb's | 216.2 Lb's | 1,875 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 9 | 32.5 | 34.1 | 40
|  |  | 460 | 3 | 9 | 16.5 | 17.3 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS047_5FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 41.6 | 45.6 | 48.2 | 50.6
R-407A ^ | 42.9 | 47.1 | 49.7 | 52.2
R-448A ^ | 42.9 | 47.1 | 49.7 | 52.2
R-449A ^ | 42.9 | 47.1 | 49.7 | 52.2
R-407C ^ | 42 | 46.2 | 48.7 | 51.2 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
5 | 30" | 1-1/2 | 1140 | 49000 | 2-1/8" | 1-5/8" | 76.8 | 75.9 Lb's | 282 Lb's | 1,900 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 9 | 32.5 | 34.1 | 40
|  |  | 460 | 3 | 9 | 16.5 | 17.3 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS056_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 49.8 | 54.6 | 57.6 | 60.5
R-407A ^ | 51.4 | 56.3 | 59.5 | 62.4
R-448A ^ | 51.4 | 56.3 | 59.5 | 62.4
R-449A ^ | 51.4 | 56.3 | 59.5 | 62.4
R-407C ^ | 50.4 | 55.2 | 58.3 | 61.2 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1-1/2 | 1140 | 58800 | 2-1/8" | 1-5/8" | 77.6 | 91 Lb's | 338.3 Lb's | 2,275 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 10.8 | 39 | 40.6 | 45
|  |  | 460 | 3 | 10.8 | 19.8 | 20.6 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS065_7FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 58.1 | 63.8 | 67.3 | 70.6
R-407A ^ | 59.9 | 65.7 | 69.4 | 72.8
R-448A ^ | 59.9 | 65.7 | 69.4 | 72.8
R-449A ^ | 59.9 | 65.7 | 69.4 | 72.8
R-407C ^ | 58.7 | 64.4 | 68 | 71.4 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
7 | 30" | 1-1/2 | 1140 | 68600 | 2-1/8" | 1-5/8" | 78.2 | 106.2 Lb's | 304.7 Lb's | 2,650 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 12.6 | 45.5 | 47.1 | 50
|  |  | 460 | 3 | 12.6 | 23.1 | 25.1 | 30
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD022_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 20.9 | 22.9 | 24.1 | 25.3
|  |  | R-407A ^ | 19.8 | 21.7 | 23 | 24.1
|  |  | R-448A ^ | 19.8 | 21.7 | 23 | 24.1
|  |  | R-449A ^ | 19.8 | 21.7 | 23 | 24.1
|  |  | R-407C ^ | 19.4 | 21.3 | 22.6 | 23.6
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 1140 | 40800 | 1-3/8" | 1-1/8" | 75.8 | 17.7 Lb's | 166.8 Lb's | 1,500 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.2 | 26 | 30.1 | 35
|  |  | 460 | 3 | 7.2 | 13.2 | 15.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD030_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 27.9 | 30.6 | 32.3 | 33.9
|  |  | R-407A ^ | 27.3 | 30 | 31.7 | 33.2
|  |  | R-448A ^ | 27.3 | 30 | 31.7 | 33.2
|  |  | R-449A ^ | 27.3 | 30 | 31.7 | 33.2
|  |  | R-407C ^ | 26.8 | 29.4 | 31.1 | 32.5
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 1140 | 40000 | 1-3/8" | 1-1/8" | 75.8 | 26.6 Lb's | 100.3 Lb's | 1,525 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.2 | 26 | 30.1 | 35
|  |  | 460 | 3 | 7.2 | 13.2 | 15.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD036_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 32.6 | 35.7 | 37.7 | 39.6
|  |  | R-407A ^ | 32.9 | 36.1 | 38.1 | 39.9
|  |  | R-448A ^ | 32.9 | 36.1 | 38.1 | 39.9
|  |  | R-449A ^ | 32.9 | 36.1 | 38.1 | 39.9
|  |  | R-407C ^ | 32.2 | 35.4 | 37.3 | 39.1
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1-1/2 | 1140 | 39200 | 1-3/8" | 1-1/8" | 75.8 | 35.3 Lb's | 355.3 Lb's | 1,550 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.2 | 26 | 30.1 | 35
|  |  | 460 | 3 | 7.2 | 13.2 | 15.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD045_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 41.8 | 45.8 | 48.4 | 50.8
|  |  | R-407A ^ | 41 | 44.9 | 47.4 | 49.8
|  |  | R-448A ^ | 41 | 44.9 | 47.4 | 49.8
|  |  | R-449A ^ | 41 | 44.9 | 47.4 | 49.8
|  |  | R-407C ^ | 40.2 | 44 | 46.5 | 48.8
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1-1/2 | 1140 | 61200 | 1-5/8" | 1-3/8" | 77.6 | 39.9 Lb's | 228 Lb's | 2,275 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 10.8 | 39 | 40.6 | 45
|  |  | 460 | 3 | 10.8 | 19.8 | 20.6 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD054_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 49 | 53.8 | 56.8 | 59.6
|  |  | R-407A ^ | 49.5 | 54.3 | 57.3 | 60.1
|  |  | R-448A ^ | 49.5 | 54.3 | 57.3 | 60.1
|  |  | R-449A ^ | 49.5 | 54.3 | 57.3 | 60.1
|  |  | R-407C ^ | 48.5 | 53.2 | 56.2 | 58.9
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1-1/2 | 1140 | 58800 | 1-5/8" | 1-3/8" | 77.6 | 53 Lb's | 195.8 Lb's | 2,300 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 10.8 | 39 | 40.6 | 45
|  |  | 460 | 3 | 10.8 | 19.8 | 20.6 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD059_8FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW |  |  |  |  | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 55.8 | 61.2 | 64.6 | 67.8
|  |  | R-407A ^ | 54.7 | 59.9 | 63.3 | 66.4
|  |  | R-448A ^ | 54.7 | 59.9 | 63.3 | 66.4
|  |  | R-449A ^ | 54.7 | 59.9 | 63.3 | 66.4
|  |  | R-407C ^ | 53.6 | 58.7 | 62 | 65.1
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
8 | 30" | 1-1/2 | 1140 | 80000 | 1-5/8" | 1-3/8" | 78.8 | 53.2 Lb's | 200.6 Lb's | 3,025 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 14.4 | 52 | 53.6 | 60
|  |  | 460 | 3 | 14.4 | 26.4 | 27.2 | 30
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD072_8FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW |  |  |  |  | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 64.7 | 71 | 74.9 | 78.6
|  |  | R-407A ^ | 65.5 | 71.8 | 75.8 | 79.5
|  |  | R-448A ^ | 65.5 | 71.8 | 75.8 | 79.5
|  |  | R-449A ^ | 65.5 | 71.8 | 75.8 | 79.5
|  |  | R-407C ^ | 64.2 | 70.4 | 74.3 | 77.9
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
8 | 30" | 1-1/2 | 1140 | 78400 | 1-5/8" | 1-3/8" | 78.8 | 70.6 Lb's | 261 Lb's | 3,050 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 14.4 | 52 | 53.6 | 60
|  |  | 460 | 3 | 14.4 | 26.4 | 27.2 | 30
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD078_10FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 71.3 | 78.2 | 82.6 | 86.6
R-407A ^ | 71.1 | 78 | 82.3 | 86.4
R-448A ^ | 71.1 | 78 | 82.3 | 86.4
R-449A ^ | 71.1 | 78 | 82.3 | 86.4
R-407C ^ | 69.7 | 76.5 | 80.7 | 84.7 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
10 | 30" | 1-1/2 | 1140 | 100000 | 2-1/8" | 1-5/8" | 79.8 | 110.9 Lb's | 432.2 Lb's | 3,775 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 18 | 65 | 66.6 | 70
|  |  | 460 | 3 | 18 | 33 | 35.1 | 40
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD094_10FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 83.3 | 91.4 | 96.5 | 101.2
R-407A ^ | 86 | 94.2 | 99.5 | 104.4
R-448A ^ | 86 | 94.2 | 99.5 | 104.4
R-449A ^ | 86 | 94.2 | 99.5 | 104.4
R-407C ^ | 84.3 | 92.3 | 97.5 | 102.3 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
10 | 30" | 1-1/2 | 1140 | 98000 | 2-1/8" | 1-5/8" | 79.8 | 151.7 Lb's | 563.9 Lb's | 3,800 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 18 | 65 | 66.6 | 70
|  |  | 460 | 3 | 18 | 33 | 35.1 | 40
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD113_12FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 99.7 | 109.3 | 115.4 | 121.1
R-407A ^ | 102.8 | 112.7 | 119 | 124.9
R-448A ^ | 102.8 | 112.7 | 119 | 124.9
R-449A ^ | 102.8 | 112.7 | 119 | 124.9
R-407C ^ | 100.8 | 110.4 | 116.6 | 122.4 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
12 | 30" | 1-1/2 | 1140 | 117600 | 2-1/8" | 1-5/8" | 80.6 | 182 Lb's | 676.6 Lb's | 4,550 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 21.6 | 78 | 80.1 | 90
|  |  | 460 | 3 | 21.6 | 39.6 | 40.4 | 45
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD131_14FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-28 14:34
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 116.2 | 127.4 | 134.5 | 141.2
R-407A ^ | 119.9 | 131.4 | 138.8 | 145.6
R-448A ^ | 119.9 | 131.4 | 138.8 | 145.6
R-449A ^ | 119.9 | 131.4 | 138.8 | 145.6
R-407C ^ | 117.5 | 128.8 | 136 | 142.7 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) # | (Winter) # | Weight
14 | 30" | 1-1/2 | 1140 | 137200 | 2-1/8" | 1-5/8" | 81.2 | 212.3 Lb's | 789.5 Lb's | 5,300 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 25.2 | 91 | 92.6 | 100
|  |  | 460 | 3 | 25.2 | 46.2 | 47 | 50
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A