## INDEX PAGE
|  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  | SUBMITTAL DATA SHEET
|  | 3885 Crestwood Parkway / Suite 500 |  |  |  | New Low Profile Unit Cooler
|  | Duluth, GA 30096 |  |  |  | Air Defrost
|  | (P) 800-288-9488 / (F) 256-259-7478 |  |  |  |  | For Record Only
|  | http://russell.htpgusa.com |  |  |  |  | For Approval
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
| 1-FAN / 6 FPI |  | RL6H035 | RL6G035 | 1-FAN / 4 FPI |  | RL4H027 | RL4H027
|  |  | RL6H042 | RL6G042 |  |  | RL4E032 | RL4E032
|  |  | RL6H049 | RL6G049 |  |  | RL4E038 | RL4E038
| 2-FAN / 6 FPI |  | RL6H066 | RL6G066 | 2-FAN / 4 FPI |  | RL4E051 | RL4E051
|  |  | RL6H077 | RL6G077 |  |  | RL4E064 | RL4E064
|  |  | RL6H090 | RL6G090 |  |  | RL4E080 | RL4E080
|  |  | RL6H105 | RL6G105 | 3-FAN / 4 FPI |  | RL4E094 | RL4E094
| 3-FAN / 6 FPI |  | RL6H121 | RL6G121 |  |  | RL4E110 | RL4E110
|  |  | RL6H142 | RL6G142 | 4-FAN / 4 FPI |  | RL4E125 | RL4E125
| 4-FAN / 6 FPI |  | RL6H162 | RL6G162 |  |  | RL4E141 | RL4E141
|  |  | RL6H182 | RL6G182 | 5-FAN / 4FPI |  | RL4E155 | RL4E155
| 5-FAN / 6FPI |  | RL6H200 | RL6G200 | 6-FAN / 4 FPI |  | RL4E195 | RL4E195
| 6-FAN / 6 FPI |  | RL6H244 | RL6G244 |  |  | RL4E230 | RL4E230
|  |  | RL6H281 | RL6G281

## 1-FAN
| Sheet1!A1 |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 09:40
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20º F & 10º TD |  | -20º F & 10º TD |  |  | Fans | Diameter
| RL6H035 | RL6G035 | 3500 |  | 4000 |  |  | 1 | 12' | 800 | 25'
| RL6H042 | RL6G042 | 4200 |  | 4900 |  |  | 1 | 12" | 785 | 25'
| RL6H049 | RL6G049 | 4900 |  | 5600 |  |  | 1 | 12" | 775 | 25'
| RL4H027 | RL4G027 | 2700 |  | 3100 |  |  | 1 | 12" | 800 | 25'
| RL4H032 | RL4G032 | 3200 |  | 3800 |  |  | 1 | 12" | 785 | 25'
| RL4H038 | RL4G038 | 3800 |  | 3800 |  |  | 1 | 12" | 775 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight Lbs. | 230v or 460v | 230v or 460v
|  | RL6H035 | RL6G035 | 6 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 0.7 | 41 | 15 | 20
|  | RL6H042 | RL6G042 | 6 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 0.7 | 44 | 15 | 20
|  | RL6H049 | RL6G049 | 6 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 1.1 | 47 | 15 | 20
|  | RL4H027 | RL4G027 | 4 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 0.7 | 40 | 15 | 20
|  | RL4H032 | RL4G032 | 4 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 0.7 | 42 | 15 | 20
|  | RL4H038 | RL4G038 | 4 | 3/8" | 5/8" | 1/4" | 3/4-14 NPT | 1.1 | 46 | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | EC Mtr | PSC Mtr | Total Motor Amps
Code |  |  |  | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
A | 115 | 1 | 60 | 0.8 | 1 | 1 | 0.8
D | 208/230 | 1 | 60 | 0.5 | 0.5 | 0.5 | 0.5
F | 460 | 1 | 60 | n/a | 0.4 | 0.4 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
New Low Profile Unit Cooler Hot Gas Subm.
1 - FAN
Hot Gas
Defrost
SUCTION
Liquid & H.G.
(2) Back & (3) Top
L
6
D
E
B
R
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
RUSSELL
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 2-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 09:40
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20º F & 10º TD |  | -20º F & 10º TD |  |  | Fans | Diameter
| RL6H066 | RL6G066 | 6600 |  | 7600 |  |  | 2 | 12' | 1600 | 25'
| RL6H077 | RL6G077 | 7700 |  | 8800 |  |  | 2 | 12" | 1570 | 25'
| RL6H090 | RL6G090 | 9000 |  | 10600 |  |  | 2 | 12" | 1550 | 25'
| RL6H105 | RL6G182 | 10500 |  | 12400 |  |  | 2 | 12" | 1550 | 25'
| RL4H051 | RL4G051 | 5100 |  | 5100 |  |  | 2 | 12" | 1600 | 25'
| RL4H064 | RL4G064 | 6400 |  | 6400 |  |  | 2 | 12" | 1570 | 25'
| RL4H080 | RL4G080 | 8000 |  | 8000 |  |  | 2 | 12" | 1550 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight Lbs. | 230v or 460v | 230v or 460v
|  | RL6H066 | RL6G066 | 6 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 1.2 | 52 | 15 | 20
|  | RL6H077 | RL6G077 | 6 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 1.5 | 55 | 15 | 20
|  | RL6H090 | RL6G090 | 6 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 1.8 | 58 | 15 | 20
|  | RL6H105 | RL6G182 | 6 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 2.1 | 62 | 15 | 20
|  | RL4H051 | RL4G051 | 4 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 1.2 | 50 | 15 | 20
|  | RL4H064 | RL4G064 | 4 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 1.5 | 52 | 15 | 20
|  | RL4H080 | RL4G080 | 4 | 3/8" | 7/8" | 1/4" | 3/4-14 NPT | 1.7 | 55 | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | EC Mtr | PSC Mtr | Total Motor Amps
Code |  |  |  | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
A | 115 | 1 | 60 | 0.8 | 1 | 2 | 1.6
D | 208/230 | 1 | 60 | 0.5 | 0.5 | 1 | 1
F | 460 | 1 | 60 | n/a | 0.4 | 0.8 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
New Low Profile Unit Cooler Hot Gas Subm.
2 - FAN
Hot Gas
Defrost
SUCTION
Liquid & H.G.
(2) Back & (3) Top
L
6
D
E
B
R
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
RUSSELL
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 3-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 09:40
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20º F & 10º TD |  | -20º F & 10º TD |  |  | Fans | Diameter
| RL6H121 | RL6G121 | 12100 |  | 14200 |  |  | 3 | 12' | 2355 | 25'
| RL6H142 | RL6G142 | 14200 |  | 16600 |  |  | 3 | 12" | 2325 | 25'
| RL4H094 | RL4G094 | 9400 |  | 9400 |  |  | 3 | 12" | 2355 | 25'
| RL4H110 | RL4G110 | 11000 |  | 11000 |  |  | 3 | 12" | 2325 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight | 230v or 460v | 230v or 460v
|  | RL6H121 | RL6G121 | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 2.5 | 78 Lb's | 15 | 20
|  | RL6H142 | RL6G142 | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 2.7 | 85 Lb's | 15 | 20
|  | RL4H094 | RL4G094 | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 2 | 79 Lb's | 15 | 20
|  | RL4H110 | RL4G110 | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 2.7 | 84 Lb's | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | EC Mtr | PSC Mtr | Total Motor Amps
Code |  |  |  | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
A | 115 | 1 | 60 | 0.8 | 1 | 3 | 2.4
D | 208/230 | 1 | 60 | 0.5 | 0.5 | 1.5 | 1.5
F | 460 | 1 | 60 | n/a | 0.4 | 1.2 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
New Low Profile Unit Cooler Hot Gas Subm.
3 - FAN
Hot Gas
Defrost
SUCTION
Liquid & H.G.
(2) Back & (3) Top
L
6
D
E
B
R
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
RUSSELL
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 4-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 09:40
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20º F & 10º TD |  | -20º F & 10º TD |  |  | Fans | Diameter
| RL6H162 | RL6G162 | 16200 |  | 18700 |  |  | 4 | 12' | 3140 | 25'
| RL6H182 | RL6G182 | 18200 |  | 21000 |  |  | 4 | 12" | 3100 | 25'
| RL4H125 | RL4G125 | 12500 |  | 14400 |  |  | 4 | 12" | 3140 | 25'
| RL4H141 | RL4G141 | 14100 |  | 14100 |  |  | 4 | 12" | 3100 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight | 230v or 460v | 230v or 460v
|  | RL6H162 | RL6G162 | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 3 | 124 Lb's | 15 | 20
|  | RL6H182 | RL6G182 | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4 | 147 Lb's | 15 | 20
|  | RL4H125 | RL4G125 | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 2.7 | 124 Lb's | 15 | 20
|  | RL4H141 | RL4G141 | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 3 | 144 Lb's | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | EC Mtr | PSC Mtr | Total Motor Amps
Code |  |  |  | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
A | 115 | 1 | 60 | 0.8 | 1 | 4 | 3.2
D | 208/230 | 1 | 60 | 0.5 | 0.5 | 2 | 2
F | 460 | 1 | 60 | n/a | 0.4 | 1.4 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
New Low Profile Unit Cooler Hot Gas Subm.
7/8 ELECTRICAL
KNOCKOUTS
SUCTION
Liquid & H.G.
(2) Back & (3) Top
L
6
D
E
B
R
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
RUSSELL
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
4 - FAN
Hot Gas
Defrost
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 5-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 09:40
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20º F & 10º TD |  | -20º F & 10º TD |  |  | Fans | Diameter
| RL6H200 | RL6G200 | 20000 |  | 22800 |  |  | 5 | 12' | 3925 | 25'
| RL4H155 | RL4G155 | 15500 |  | 17700 |  |  | 5 | 12" | 3925 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight | 230v or 460v | 230v or 460v
|  | RL6H200 | RL6G200 | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.9 | 195 Lb's | 15 | 20
|  | RL4H155 | RL4G155 | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4 | 191 Lb's | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | EC Mtr | PSC Mtr | Total Motor Amps
Code |  |  |  | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
A | 115 | 1 | 60 | 0.8 | 1 | 5 | 4
D | 208/230 | 1 | 60 | 0.5 | 0.5 | 2.5 | 2.5
F | 460 | 1 | 60 | n/a | 0.4 | 2 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
New Low Profile Unit Cooler Hot Gas Subm.
SUCTION
Liquid & H.G.
(2) Back & (3) Top
5 - FAN
Hot Gas
Defrost
L
6
D
E
B
R
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
RUSSELL
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## 6-FAN
|  |  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | New Low Profile Unit Cooler
|  |  |  | Duluth, GA 30096 |  |  |  |  | Air Defrost
|  |  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  |  | http://russell.htpgusa.com | [5 empty] | For Approval
| Job Name: | [5 empty] | Job Location:
| Customer Name: | [5 empty] | Order Number:
| Architect / Engineer: | [5 empty] | Prepared By:
| Unit Model Number: | [5 empty] | Tagging Info:
| Unit Quantity: | [5 empty] | Date: |  | 2017-07-26 09:40
CAPACITY (BTUH) @ 10 DEG TD
| UNIT MODEL |  | Saturated Suction Temp (SST) |  |  |  |  | FAN DATA
|  |  | R-404A |  | R-407A & R-448A/R-449A |  |  | Qty | Fan | CFM | Air Throw
|  |  | -20º F & 10º TD |  | -20º F & 10º TD |  |  | Fans | Diameter
| RL6H244 | RL6G244 | 24400 |  | 27900 |  |  | 6 | 12' | 4710 | 25'
| RL6H281 | RL6G281 | 28100 |  | 33000 |  |  | 6 | 12" | 4650 | 25'
| RL4H195 | RL4G195 | 19500 |  | 22300 |  |  | 6 | 12" | 4710 | 25'
| RL4H230 | RL4G230 | 23000 |  | 27000 |  |  | 6 | 12" | 4650 | 25'
PHYSICAL DATA
|  | Unit |  | FPI | Refrig Conn (ODS) |  |  | Drain | Refrig | Net | MCA | MOPD
|  | Model |  |  | Liquid | Suction | Ext Equal | Conn | Charge | Weight | 230v or 460v | 230v or 460v
|  | RL6H244 | RL6G244 | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 5.2 | 238 Lb's | 15 | 20
|  | RL6H281 | RL6G281 | 6 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 5.9 | 262 Lb's | 15 | 20
|  | RL4H195 | RL4G195 | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.5 | 257 Lb's | 15 | 20
|  | RL4H230 | RL4G230 | 4 | 3/8" | 1-1/8" | 1/4" | 3/4-14 NPT | 4.9 | 262 Lb's | 15 | 20
ELECTRICAL DATA
Voltage | Voltage | Phase | Hertz | EC Mtr | PSC Mtr | Total Motor Amps
Code |  |  |  | Amps Ea | Amps Ea | PSC Mtrs | EC Mtrs
A | 115 | 1 | 60 | 0.8 | 1 | 6 | 4.8
D | 208/230 | 1 | 60 | 0.5 | 0.5 | 3 | 3
F | 460 | 1 | 60 | n/a | 0.4 | 2.4 | N/A
| Additional Comments: |  | Refrigerant charge listed is approximate in pounds of R-404A.
New Low Profile Unit Cooler Hot Gas Subm.
7/8 ELECTRICAL
KNOCKOUTS
6 - FAN
Hot Gas
Defrost
Liquid & H.G.
(2) Back & (3) Top
SUCTION
L
6
D
E
B
R
A
068
A
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
RUSSELL
Fins Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Single Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuration descriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625

## Model Nomenclature
R
L
6
E
042
D
E
A
B
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
RUSSELL
FIns Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Singel Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuratidescriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
R
L
6
H
042
D
E
A
B
L
Refrigerant Type
A=R404A E = R448A/R449A
B = R407A F = CO2 DX
C = R407C G = Clycol (consult factory)
D = R407F
Revision Code
Model Type
L=Low Profile
RUSSELL
FIns Per inch
4 FPI
6 FPI
Type of Defrost
A=Air Defrost
E=Electric Defrost
H=Hot Gas 3-Pipe
G=Hot GasRev.Cycle 2 Pipe
BTUH In Hundreds
Motor Type
P = PSC
E = Singel Speed ECM
D = Dual Speed ECM
Pre-Assembly Code
Blank = Standard Configuration
T = mounted TXV only
L = mounted TXV, LLS, T-Stat
M = Master COnfiguration with TXV, LLS,
T-Stat and copper tee
See features page for configuratidescriptions
Voltage Code
A = 115/1/60 L = 100/1/50
D = 208-230/1/60 M = 200-220/1/50
E = 208-230/3/60 N = 200-220/3/50
F = 460/1/60 P = 380/1/50
Capacity Correction for Electric & hot Gas Defrost Evaporators
SST (Dew)
Factor:
1.15
𝟐𝟎℉
𝟎℉
−𝟏𝟎℉
-20
-20℉
-30
-30℉
1.075
1.0375
1
.9625