## SUB_INDEX
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  | SUBMITTAL DATA INDEX
|  |  | 3885 Crestwood Parkway / Suite 500 |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  | MultiCon
(P) 800-288-9488 / (F) 256-259-7478
|  |  | http://russell.htpgusa.com |  | Small Air Cooled Condenser
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
SUBMITTAL DATA INDEX
|  |  | 850 RPM MODELS | 1075 RPM MODELS
|  |  | RDS001*C1B12A1A | RDS001*A1B12A1A
|  |  | RDS002*C1B12A1A | RDS002*A1B12A1A
|  |  | RDS003*C1B12A1A | RDS003*A1B12A1A
RDS004*C1B12A1A
RDS005*A1B12A1A
RDS006*C2B12A1A
RDS007*A2B12A1A
RDS008*C2B12A1A
|  |  | RDS009*C2B12A1A | RDS009*A2B12A1A
RDS011*A2B12A1A
MODEL NUMBER KEY
R D S 001 E A 1 B 1 2 A 1 A
R = Russell | [6 empty] | A = Revison Code
D = Condenser | [6 empty] | Circuiting
1 = Full
S = Single Wide | [6 empty] | 2 = 50/50
X = Other
Capacity = MBH / THR
Per Degree TD / 10 FPI | [5 empty] | Design Config
Vertical Disch / Std Legs
| Voltage Code |  |  |  |  | Vertical Disch / 30" Legs
| E = 208/230/3/60 |  |  |  |  | Horizontal Disch / Std Legs
G = 460/3/60
| J = 575/3/60 |  |  |  |  | Housing Material / Coating
| N = 200/220/3/50 |  |  |  |  | 1 = Aluminum
| Q = 380/3/50 |  |  |  |  | 2 = Galvanized
| X = Other |  | Motor RPM / HP |  |  | 7 - 316L Stainless Steel
|  |  | A = 1075 / 1/3 HP |  |  | X = Other
C = 850 / 1/4 HP
Coil Matl / Coating Options
|  | Fans Long (1 or 2) |  |  | 1 = Aluminum Fins
2 = Copper Fins
|  | Fin Spacing |  |  | 3 = Alum + AST Coating
|  | A = 8 FPI |  |  | 6 = Alum + Heresite Coating
|  | B = 10 FPI |  |  | 7 = Alum + Poly Fin Coating
|  | C = 12 FPI |  |  | X = Other
D = 14 FPI
X = Other
SMALL_RDS_INDEX_1116_NEW

## RDS001_A1
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 0.73 | 0.84 | 0.9 | 1.04
|  |  | R-407A ^ | 0.67 | 0.77 | 0.82 | 0.95
|  |  | R-407C ^ | 0.66 | 0.76 | 0.8 | 0.93
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 18" | 1/3 | 1075 | 3020 | 7/8" | 7/8" | 47 | .42 Lb's | 1.14 Lb's | 80 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.28 | 3.2 | 15 | 15
|  |  | 208/230 | 3 | 0.28 | 1.8 | 15 | 15
|  |  | 460 | 1 | 0.28 | 1.3 | 15 | 15
|  |  | 460 | 3 | 0.28 | 0.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS001_C1
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 0.68 | 0.79 | 0.88 | 0.97
|  |  | R-407A ^ | 0.63 | 0.73 | 0.81 | 0.9
|  |  | R-407C ^ | 0.67 | 0.72 | 0.79 | 0.88
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 18" | 1/4 | 850 | 2470 | 7/8" | 7/8" | 47 | .42 Lb's | 1.14 Lb's | 80 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.11 | 1.4 | 15 | 15
|  |  | 208/230 | 3 | 0.11 | 1.1 | 15 | 15
|  |  | 460 | 1 | 0.11 | 0.7 | 15 | 15
|  |  | 460 | 3 | 0.11 | 0.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS002_A1
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 1.17 | 1.33 | 1.45 | 1.57
|  |  | R-407A ^ | 1.16 | 1.26 | 1.38 | 1.48
|  |  | R-407C ^ | 1.18 | 1.24 | 1.35 | 1.45
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 18" | 1/3 | 1075 | 2840 | 7/8" | 7/8" | 47 | 0.83 Lb's | 2.25 Lb's | 86 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.28 | 3.2 | 15 | 15
|  |  | 208/230 | 3 | 0.28 | 1.8 | 15 | 15
|  |  | 460 | 1 | 0.28 | 1.3 | 15 | 15
|  |  | 460 | 3 | 0.28 | 0.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS002_C1
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 1.09 | 1.24 | 1.36 | 1.47
|  |  | R-407A ^ | 1.05 | 1.19 | 1.31 | 1.41
|  |  | R-407C ^ | 1.03 | 1.17 | 1.28 | 1.38
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 18" | 1/4 | 850 | 2110 | 7/8" | 7/8" | 47 | 0.83 Lb's | 2.25 Lb's | 86 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.11 | 1.4 | 15 | 15
|  |  | 208/230 | 3 | 0.11 | 1.1 | 15 | 15
|  |  | 460 | 1 | 0.11 | 0.7 | 15 | 15
|  |  | 460 | 3 | 0.11 | 0.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS003_A1
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 1.6 | 1.81 | 1.99 | 2.15
|  |  | R-407A ^ | 1.52 | 1.72 | 1.89 | 2.04
|  |  | R-407C ^ | 1.49 | 1.69 | 1.85 | 2
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 22" | 1/3 | 1075 | 4450 | 7/8" | 7/8" | 57 | 1.12 Lb's | 3.0 Lb's | 107 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.47 | 3.2 | 15 | 15
|  |  | 208/230 | 3 | 0.47 | 1.8 | 15 | 15
|  |  | 460 | 1 | 0.47 | 1.3 | 15 | 15
|  |  | 460 | 3 | 0.47 | 0.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS003_C1
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 1.44 | 1.63 | 1.79 | 1.93
|  |  | R-407A ^ | 1.38 | 1.57 | 1.72 | 1.86
|  |  | R-407C ^ | 1.35 | 1.54 | 1.69 | 1.82
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 22" | 1/4 | 850 | 3290 | 7/8" | 7/8" | 52 | 1.12 Lb's | 3.0 Lb's | 107 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.2 | 1.4 | 15 | 15
|  |  | 208/230 | 3 | 0.2 | 1.1 | 15 | 15
|  |  | 460 | 1 | 0.2 | 0.7 | 15 | 15
|  |  | 460 | 3 | 0.2 | 0.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS004_C1
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 1.97 | 2.19 | 2.35 | 2,49
|  |  | R-407A ^ | 1.81 | 2.02 | 2.16 | 2.29
|  |  | R-407C ^ | 1.77 | 1.98 | 2.12 | 2.24
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 22" | 1/4 | 850 | 2880 | 7/8" | 7/8" | 52 | 1.82 Lb's | 4.9 Lb's | 116 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.2 | 1.4 | 15 | 15
|  |  | 208/230 | 3 | 0.2 | 1.1 | 15 | 15
|  |  | 460 | 1 | 0.2 | 0.7 | 15 | 15
|  |  | 460 | 3 | 0.2 | 0.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS005_A1
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 2.23 | 2.48 | 2.68 | 2.81
|  |  | R-407A ^ | 2.18 | 2.43 | 2.61 | 2.75
|  |  | R-407C ^ | 2.14 | 2.38 | 2.56 | 2.7
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 22" | 1/3 | 1075 | 3900 | 7/8" | 7/8" | 57 | 1.82 Lb's | 4.9 Lb's | 116 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.47 | 3.2 | 15 | 15
|  |  | 208/230 | 3 | 0.47 | 1.8 | 15 | 15
|  |  | 460 | 1 | 0.47 | 1.3 | 15 | 15
|  |  | 460 | 3 | 0.47 | 0.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS006_C2
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 3.09 | 3.51 | 3.86 | 4.16
|  |  | R-407A ^ | 2.97 | 3.37 | 3.71 | 4
|  |  | R-407C ^ | 2.91 | 3.3 | 3.64 | 3.92
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 22" | 1/4 | 850 | 6390 | 1-1/8" | 1-1/8" | 55 | 2.24 Lb's | 6.1 Lb's | 164 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.4 | 2.8 | 15 | 15
|  |  | 208/230 | 3 | 0.4 | 2.2 | 15 | 15
|  |  | 460 | 1 | 0.4 | 1.4 | 15 | 15
|  |  | 460 | 3 | 0.4 | 1.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS007_A2
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 3.42 | 3.89 | 4.27 | 4.6
|  |  | R-407A ^ | 3.25 | 3.69 | 4.05 | 4.37
|  |  | R-407C ^ | 3.19 | 3.62 | 3.97 | 4.28
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 22" | 1/3 | 1075 | 8640 | 1-1/8" | 1-1/8" | 60 | 2.24 Lb's | 6.1 Lb's | 164 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.94 | 6.4 | 15 | 15
|  |  | 208/230 | 3 | 0.94 | 3.6 | 15 | 15
|  |  | 460 | 1 | 0.94 | 2.6 | 15 | 15
|  |  | 460 | 3 | 0.94 | 1.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS008_C2
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 4.05 | 4.51 | 4.83 | 5.11
|  |  | R-407A ^ | 4.04 | 4.5 | 4.82 | 5.1
|  |  | R-407C ^ | 3.96 | 4.41 | 4.73 | 5
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 22" | 1/4 | 850 | 5760 | 1-1/8" | 1-1/8" | 55 | 2.24 Lb's | 6.1 Lb's | 179 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.4 | 2.8 | 15 | 15
|  |  | 208/230 | 3 | 0.4 | 2.2 | 15 | 15
|  |  | 460 | 1 | 0.4 | 1.4 | 15 | 15
|  |  | 460 | 3 | 0.4 | 1.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS009_A2
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 5.46 | 5.06 | 5.45 | 5.76
|  |  | R-407A ^ | 4.47 | 4.98 | 5.34 | 5.64
|  |  | R-407C ^ | 4.38 | 4.88 | 5.23 | 5.53
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 22" | 1/3 | 1075 | 7780 | 1-1/8" | 1-1/9" | 60 | 4.56 Lb's | 12.31 Lb's | 179 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.94 | 6.4 | 15 | 15
|  |  | 208/230 | 3 | 0.94 | 3.6 | 15 | 15
|  |  | 460 | 1 | 0.94 | 2.6 | 15 | 15
|  |  | 460 | 3 | 0.94 | 1.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS009_C2
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 4.53 | 4.94 | 5.21 | 5.5
|  |  | R-407A ^ | 4.69 | 5.12 | 5.39 | 5.7
|  |  | R-407C ^ | 4.6 | 5.02 | 5.28 | 5.59
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 22" | 1/4 | 850 | 5170 | 1-1/8" | 1-1/8" | 55 | 4.56 Lb's | 12.31 Lb's | 195 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.4 | 2.8 | 15 | 15
|  |  | 208/230 | 3 | 0.4 | 2.2 | 15 | 15
|  |  | 460 | 1 | 0.4 | 1.4 | 15 | 15
|  |  | 460 | 3 | 0.4 | 1.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A

## RDS011_A2
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Small Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2017-04-18 14:51
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 5.31 | 5.79 | 6.1 | 6.45
|  |  | R-407A ^ | 5.37 | 5.85 | 6.16 | 6.52
|  |  | R-407C ^ | 5.26 | 5.73 | 6.04 | 6.39
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 22" | 1/3 | 1075 | 7080 | 1-1/8" | 1-1/8" | 60 | 4.56 Lb's | 12.31 Lb's | 195 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 1 | 0.94 | 6.4 | 15 | 15
|  |  | 208/230 | 3 | 0.94 | 3.6 | 15 | 15
|  |  | 460 | 1 | 0.94 | 2.6 | 15 | 15
|  |  | 460 | 3 | 0.94 | 1.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A / R-407C @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
SM_ACC_SBMTL_1116-A