## SUB_INDEX
|  | HEAT TRANSFER PRODUCTS GROUP, LLC |  | SUBMITTAL DATA INDEX
|  | 3885 Crestwood Parkway / Suite 500 |  | Model Series - WDS / WDD
|  | Duluth, GA 30096 |  | QUANTUM AIR
(P) 800-288-9488 / (F) 256-259-7478
|  | http://witt.htpgusa.com |  | Remote - Air Cooled Condenser
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
SUBMITTAL DATA INDEX
1/3 HP / 550 RPM MODELS
|  | SINGLE WIDE MODELS | DOUBLE WIDE MODELS
|  | WDS004*B1A | WDD016*B2A
|  | WDS005*B1A | WDD021*B2A
|  | WDS006*B1A | WDD025*B2A
|  | WDS008*B2A | WDD032*B3A
|  | WDS011*B2A | WDD037*B3A
|  | WDS012*B2A | WDD043*B4A
|  | WDS016*B3A | WDD050*B4A
|  | WDS018*B3A | WDD055*B5A
|  | WDS021*B4A | WDD063*B5A
|  | WDS025*B4A | WDD080*B6A
|  | WDS028*B5A | WDD093*B7A
WDS032*B5A
WDS040*B6A
WDS046*B7A
MODEL NUMBER KEY
W D S 004 E E 1 A
A = Revison Code
W = Witt
# Fans Long
1 thru 7
| D = Condenser |  |  | Motor RPM / HP
B = 1140 / 1.5 HP
D = 850 / 1.5 HP
| S = Single Wide |  |  | L = 850 / 1 HP
| D = Double Wide |  |  | E = 550 / 1/3 HP
Voltage Code
| Capacity = MBH / THR |  |  | E = 208/230/3/60
| Per Degree TD / 10 FPI |  |  | G = 460/3/60
J = 575/3/60
N = 200/220/3/50
Q = 380/3/50
X = Other
WDS_WDD_INDEX_1116_NEW

## WDS004_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 3.7 | 4.1 | 4.3 | 4.5
|  |  | R-407A ^ | 3.7 | 4 | 4.2 | 4.4
|  |  | R-448A ^ | 3.7 | 4 | 4.2 | 4.4
|  |  | R-449A ^ | 3.7 | 4 | 4.2 | 4.4
|  |  | R-407C ^ | 3.6 | 3.9 | 4.1 | 4.3
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1/3 | 550 | 5300 | 1-1/8" | 7/8" | 49.4 | 4.5 Lb's | 16.7 Lb's | 350 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 0.4 | 2.8 | 15 | 15
|  |  | 460 | 3 | 0.4 | 1.4 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS005_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 4.8 | 5.3 | 5.6 | 5.9
|  |  | R-407A ^ | 4.9 | 5.4 | 5.7 | 6
|  |  | R-448A ^ | 4.9 | 5.4 | 5.7 | 6
|  |  | R-449A ^ | 4.9 | 5.4 | 5.7 | 6
|  |  | R-407C ^ | 4.8 | 5.3 | 5.6 | 5.9
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1/3 | 550 | 5200 | 1-1/8" | 7/8" | 49.4 | 6.6 Lb's | 25 Lb's | 375 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 0.4 | 2.8 | 15 | 15
|  |  | 460 | 3 | 0.4 | 1.4 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS006_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 5.3 | 5.8 | 6.1 | 6.4
|  |  | R-407A ^ | 5.7 | 6.2 | 6.6 | 6.9
|  |  | R-448A ^ | 5.7 | 6.2 | 6.6 | 6.9
|  |  | R-449A ^ | 5.7 | 6.2 | 6.6 | 6.9
|  |  | R-407C ^ | 5.6 | 6.1 | 6.5 | 6.8
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | 1/3 | 550 | 5100 | 1-1/8" | 7/8" | 49.4 | 8.8 Lb's | 32.6 Lb's | 400 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 0.4 | 2.8 | 15 | 15
|  |  | 460 | 3 | 0.4 | 1.4 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS008_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 7.5 | 8.2 | 8.7 | 9.1
|  |  | R-407A ^ | 7.4 | 8.1 | 8.6 | 9
|  |  | R-448A ^ | 7.4 | 8.1 | 8.6 | 9
|  |  | R-449A ^ | 7.4 | 8.1 | 8.6 | 9
|  |  | R-407C ^ | 7.3 | 7.9 | 8.4 | 8.8
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1/3 | 550 | 10600 | 1-3/8" | 1-1/8" | 52.4 | 8.8 Lb's | 33.2 Lb's | 725 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 0.7 | 5.6 | 15 | 15
|  |  | 460 | 3 | 0.7 | 2.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS011_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 9.6 | 10.5 | 11.1 | 11.6
|  |  | R-407A ^ | 9.8 | 10.7 | 11.3 | 11.9
|  |  | R-448A ^ | 9.8 | 10.7 | 11.3 | 11.9
|  |  | R-449A ^ | 9.8 | 10.7 | 11.3 | 11.9
|  |  | R-407C ^ | 9.6 | 10.5 | 11.1 | 11.7
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1/3 | 550 | 10400 | 1-3/8" | 1-1/8" | 52.4 | 13.3 Lb's | 50.1 Lb's | 750 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 0.7 | 5.6 | 15 | 15
|  |  | 460 | 3 | 0.7 | 2.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS012_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 10.5 | 11.5 | 12.2 | 12.7
|  |  | R-407A ^ | 11.2 | 12.3 | 13 | 13.6
|  |  | R-448A ^ | 11.2 | 12.3 | 13 | 13.6
|  |  | R-449A ^ | 11.2 | 12.3 | 13 | 13.6
|  |  | R-407C ^ | 11 | 12.1 | 12.7 | 13.3
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | 1/3 | 550 | 10200 | 1-3/8" | 1-1/8" | 52.4 | 17.7 Lb's | 65.3 Lb's | 775 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 0.7 | 5.6 | 15 | 15
|  |  | 460 | 3 | 0.7 | 2.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS016_3FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 14.4 | 15.8 | 16.7 | 17.5
|  |  | R-407A ^ | 14.8 | 16.2 | 17.1 | 17.9
|  |  | R-448A ^ | 14.8 | 16.2 | 17.1 | 17.9
|  |  | R-449A ^ | 14.8 | 16.2 | 17.1 | 17.9
|  |  | R-407C ^ | 14.5 | 15.9 | 16.8 | 17.6
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
3 | 30" | 1/3 | 550 | 15600 | 1-5/8" | 1-3/8" | 54.2 | 19.9 Lb's | 75.2 Lb's | 1,125 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.1 | 8.4 | 15 | 15
|  |  | 460 | 3 | 1.1 | 4.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS018_3FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 15.8 | 17.3 | 18.3 | 19.2
|  |  | R-407A ^ | 16.8 | 18.4 | 19.4 | 20.4
|  |  | R-448A ^ | 16.8 | 18.4 | 19.4 | 20.4
|  |  | R-449A ^ | 16.8 | 18.4 | 19.4 | 20.4
|  |  | R-407C ^ | 16.5 | 18 | 19 | 20
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
3 | 30" | 1/3 | 550 | 15300 | 1-5/8" | 1-3/8" | 54.2 | 26.5 Lb's | 97.9 Lb's | 1,150 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.1 | 8.4 | 15 | 15
|  |  | 460 | 3 | 1.1 | 4.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS021_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 19.1 | 20.9 | 22.1 | 23.2
|  |  | R-407A ^ | 19.5 | 21.4 | 22.6 | 23.7
|  |  | R-448A ^ | 19.5 | 21.4 | 22.6 | 23.7
|  |  | R-449A ^ | 19.5 | 21.4 | 22.6 | 23.7
|  |  | R-407C ^ | 13.1 | 21 | 22.2 | 23.2
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1/3 | 550 | 20800 | 1-5/8" | 1-3/8" | 55.4 | 26.6 Lb's | 100.3 Lb's | 1,500 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.4 | 11.2 | 15 | 15
|  |  | 460 | 3 | 1.4 | 5.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS025_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 21.3 | 23.3 | 24.6 | 25.8
|  |  | R-407A ^ | 22.6 | 24.8 | 26.2 | 27.5
|  |  | R-448A ^ | 22.6 | 24.8 | 26.2 | 27.5
|  |  | R-449A ^ | 22.6 | 24.8 | 26.2 | 27.5
|  |  | R-407C ^ | 22.2 | 24.3 | 25.7 | 27
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1/3 | 550 | 20400 | 1-5/8" | 1-3/8" | 55.4 | 35.3 Lb's | 130.6 Lb's | 1,525 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.4 | 11.2 | 15 | 15
|  |  | 460 | 3 | 1.4 | 5.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS028_5FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 24 | 26.3 | 27.8 | 29.1
R-407A ^ | 25.3 | 27.7 | 29.3 | 30.7
R-448A ^ | 25.3 | 27.7 | 29.3 | 30.7
R-449A ^ | 25.3 | 27.7 | 29.3 | 30.7
R-407C ^ | 24.8 | 27.2 | 28.7 | 30.1 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
5 | 30" | 1/3 | 550 | 26000 | 2-1/8" | 1-5/8" | 56.4 | 55.5 Lb's | 216.2 Lb's | 1,875 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.8 | 14 | 15.1 | 20
|  |  | 460 | 3 | 1.8 | 7 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS032_5FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 26.5 | 29.1 | 30.7 | 32.2
R-407A ^ | 28.8 | 31.6 | 33.4 | 35
R-448A ^ | 28.8 | 31.6 | 33.4 | 35
R-449A ^ | 28.8 | 31.6 | 33.4 | 35
R-407C ^ | 28.2 | 31 | 32.7 | 34.3 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
5 | 30" | 1/3 | 550 | 25500 | 2-1/8" | 1-5/8" | 56.4 | 75.9 Lb's | 282 Lb's | 1,900 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.8 | 14 | 15.1 | 20
|  |  | 460 | 3 | 1.8 | 7 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS040_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 33.5 | 36.7 | 38.8 | 40.7
R-407A ^ | 36.4 | 39.9 | 42.1 | 44.2
R-448A ^ | 36.4 | 39.9 | 42.1 | 44.2
R-449A ^ | 36.4 | 39.9 | 42.1 | 44.2
R-407C ^ | 35.7 | 39.1 | 41.6 | 43.3 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1/3 | 550 | 30600 | 2-1/8" | 1-5/8" | 57.2 | 91 Lb's | 338.3 Lb's | 2,275 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.1 | 16.8 | 17.5 | 20
|  |  | 460 | 3 | 2.1 | 8.4 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDS046_7FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 39 | 42.7 | 45.1 | 47.3
R-407A ^ | 42.4 | 46.4 | 49 | 51.4
R-448A ^ | 42.4 | 46.4 | 49 | 51.4
R-449A ^ | 42.4 | 46.4 | 49 | 51.4
R-407C ^ | 41.6 | 45.5 | 48 | 50.4 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
7 | 30" | 1/3 | 550 | 35700 | 2-1/8" | 1-5/8" | 57.8 | 106.2 Lb's | 304.7 Lb's | 2,650 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.5 | 19.6 | 20.3 | 25
|  |  | 460 | 3 | 2.5 | 9.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD016_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 14.9 | 16.3 | 17.2 | 18.1
|  |  | R-407A ^ | 14.6 | 16 | 16.9 | 17.7
|  |  | R-448A ^ | 14.6 | 16 | 16.9 | 17.7
|  |  | R-449A ^ | 14.6 | 16 | 16.9 | 17.7
|  |  | R-407C ^ | 14.3 | 15.7 | 16.6 | 17.4
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1/3 | 550 | 21200 | 1-3/8" | 1-1/8" | 55.4 | 17.7 Lb's | 166.8 Lb's | 1,500 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.4 | 11.2 | 15 | 15
|  |  | 460 | 3 | 7.2 | 5.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD021_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 19.1 | 20.9 | 22.1 | 23.2
|  |  | R-407A ^ | 19.5 | 21.4 | 22.6 | 23.7
|  |  | R-448A ^ | 19.5 | 21.4 | 22.6 | 23.7
|  |  | R-449A ^ | 19.5 | 21.4 | 22.6 | 23.7
|  |  | R-407C ^ | 19.1 | 21 | 22.2 | 23.2
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1/3 | 550 | 20800 | 1-3/8" | 1-1/8" | 55.4 | 26.6 Lb's | 100.3 Lb's | 1,525 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.4 | 11.2 | 15 | 15
|  |  | 460 | 3 | 1.4 | 5.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD025_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 21.1 | 23.1 | 24.4 | 25.6
|  |  | R-407A ^ | 22.5 | 24.6 | 26 | 27.3
|  |  | R-448A ^ | 22.5 | 24.6 | 26 | 27.3
|  |  | R-449A ^ | 22.5 | 24.6 | 26 | 27.3
|  |  | R-407C ^ | 22.1 | 24.1 | 25.5 | 26.8
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | 1/3 | 550 | 20400 | 1-3/8" | 1-1/8" | 55.4 | 35.3 Lb's | 355.3 Lb's | 1,550 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.4 | 11.2 | 15 | 15
|  |  | 460 | 3 | 1.4 | 5.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD032_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 28.7 | 31.5 | 33.3 | 34.9
|  |  | R-407A ^ | 29.5 | 32.3 | 34.1 | 35.8
|  |  | R-448A ^ | 29.5 | 32.3 | 34.1 | 35.8
|  |  | R-449A ^ | 29.5 | 32.3 | 34.1 | 35.8
|  |  | R-407C ^ | 28.9 | 31.7 | 33.4 | 35.1
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1/3 | 550 | 31200 | 1-5/8" | 1-3/8" | 57.2 | 39.9 Lb's | 228 Lb's | 2,275 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.1 | 16.8 | 17.5 | 20
|  |  | 460 | 3 | 2.1 | 8.4 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD037_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 31.5 | 34.5 | 36.5 | 38.2
|  |  | R-407A ^ | 33.6 | 36.8 | 38.9 | 40.8
|  |  | R-448A ^ | 33.6 | 36.8 | 38.9 | 40.8
|  |  | R-449A ^ | 33.6 | 36.8 | 38.9 | 40.8
|  |  | R-407C ^ | 32.9 | 36.1 | 38.1 | 40
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | 1/3 | 550 | 30600 | 1-5/8" | 1-3/8" | 57.2 | 53 Lb's | 195.8 Lb's | 2,300 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.1 | 16.8 | 17.5 | 20
|  |  | 460 | 3 | 2.1 | 8.4 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD043_8FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW |  |  |  |  | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 38.1 | 41.8 | 44.2 | 46.3
|  |  | R-407A ^ | 39.1 | 42.8 | 45.2 | 47.4
|  |  | R-448A ^ | 39.1 | 42.8 | 45.2 | 47.4
|  |  | R-449A ^ | 39.1 | 42.8 | 45.2 | 47.4
|  |  | R-407C ^ | 38.3 | 42.4 | 44.3 | 46.5
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
8 | 30" | 1/3 | 550 | 41600 | 1-5/8" | 1-3/8" | 58.4 | 53.2 Lb's | 200.6 Lb's | 3,025 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.8 | 22.4 | 25.1 | 30
|  |  | 460 | 3 | 2.8 | 11.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD050_8FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW |  |  |  |  | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 42.4 | 46.5 | 49.1 | 5105
|  |  | R-407A ^ | 45.2 | 49.5 | 52.3 | 54.8
|  |  | R-448A ^ | 45.2 | 49.5 | 52.3 | 54.8
|  |  | R-449A ^ | 45.2 | 49.5 | 52.3 | 54.8
|  |  | R-407C ^ | 44.3 | 48.5 | 51.3 | 53.7
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
8 | 30" | 1/3 | 550 | 41600 | 1-5/8" | 1-3/8" | 58.4 | 70.6 Lb's | 261 Lb's | 3,050 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.8 | 22.4 | 25.1 | 30
|  |  | 460 | 3 | 2.8 | 11.2 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD055_10FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 48.3 | 53 | 56 | 58.7
R-407A ^ | 50.5 | 55.3 | 58.4 | 61.3
R-448A ^ | 50.5 | 55.3 | 58.4 | 61.3
R-449A ^ | 50.5 | 55.3 | 58.4 | 61.3
R-407C ^ | 49.5 | 54.2 | 57.2 | 60.1 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
10 | 30" | 1/3 | 550 | 52000 | 2-1/8" | 1-5/8" | 59.4 | 110.9 Lb's | 432.2 Lb's | 3,775 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 3.5 | 28 | 30.1 | 35
|  |  | 460 | 3 | 3.5 | 14 | 15.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD063_10FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 53.1 | 58.2 | 61.5 | 64.5
R-407A ^ | 57.8 | 63.6 | 66.8 | 70.1
R-448A ^ | 57.8 | 63.6 | 66.8 | 70.1
R-449A ^ | 57.8 | 63.6 | 66.8 | 70.1
R-407C ^ | 56.7 | 62.3 | 65.5 | 68.7 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
10 | 30" | 1/3 | 550 | 51000 | 2-1/8" | 1-5/8" | 59.4 | 151.7 Lb's | 563.9 Lb's | 3,800 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 3.5 | 28 | 30.1 | 35
|  |  | 460 | 3 | 3.5 | 14 | 15.1 | 20
Notes
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD080_12FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 67 | 73.5 | 77.7 | 81.4
R-407A ^ | 72.8 | 79.8 | 84.3 | 88.4
R-448A ^ | 72.8 | 79.8 | 84.3 | 88.4
R-449A ^ | 72.8 | 79.8 | 84.3 | 88.4
R-407C ^ | 71.3 | 78.2 | 82.6 | 86.6 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
12 | 30" | 1/3 | 550 | 61200 | 2-1/8" | 1-5/8" | 60.2 | 182 Lb's | 676.6 Lb's | 4,550 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.2 | 33.6 | 35.1 | 40
|  |  | 460 | 3 | 4.2 | 16.8 | 17.2 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## WDD093_14FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - WDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://witt.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 09:13
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 77.8 | 85.3 | 90.1 | 94.5
R-407A ^ | 84.6 | 92.7 | 97.9 | 102.7
R-448A ^ | 84.6 | 92.7 | 97.9 | 102.7
R-449A ^ | 84.6 | 92.7 | 97.9 | 102.7
R-407C ^ | 82.9 | 91 | 95.9 | 100.7 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | HP | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) # | (Winter) # | Weight
14 | 30" | 1/3 | 550 | 71400 | 2-1/8" | 1-5/8" | 60.8 | 212.3 Lb's | 789.5 Lb's | 5,300 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.9 | 39.2 | 40.1 | 45
|  |  | 460 | 3 | 4.9 | 19.6 | 20.1 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A